## readiness
Refinery Unit | Area | Unit | Tag Number | Type Tangki | Service Tangki | Prioritas | Status Operational Tangki | Cert No ATG | Date Expired ATG | ATG Certification Validity | COI (Date Expired) | No COI | Status COI | Internal Inspection | Plan Internal Inspection | Date Expired (Validity Volume Table Tank (Tera)) | Status Validity Volume Table Tank (Tera) | Cert No Validity Volume Table Tank (Tera) | Status ATG | Caption Status | Remark ATG | RTL ATG | Status Grounding | Caption Status | Remark Grounding | RTL Grounding | Status Bonding | Caption Status | Remark Bonding | RTL Bonding | Status Temperature Indicator | Caption Status | Remark Temperature Indicator | RTL Temperature Indicator | Status Level Indikator | Caption Status | Remark Level Indikator | RTL Level Indikator | Status Gauge Gatch (Tutup Lubang Sample) | Caption Status | Remark Gauge Gatch (Tutup Lubang Sample) | RTL Gauge Gatch (Tutup Lubang Sample) | Status Alarm System | Caption Status | Remark Alarm System | RTL Alarm System | Status IHLA | Caption Status | Remark IHLA | RTL IHLA | Status Instalasi Water Sprinkle | Caption Status | Remark Instalasi Water Sprinkle | RTL Instalasi Water Sprinkle | Status Instalasi Foam Chamber | Caption Status | Remark Instalasi Foam Chamber | RTL Instalasi Foam Chamber | Status Gun Monitor | Caption Status | Remark Gun Monitor | RTL Gun Monitor | Status FGDS | Caption Status | Remark FGDS | RTL FGDS | Status LPS | Caption Status | Remark LPS | RTL LPS | Status Cathodic Protection | Caption Status | Remark Cathodic Protection | RTL Cathodic Protection | Status Shell Course | Caption Status | Remark Shell Course | RTL Shell Course | Status Roof (cone/Floating) | Caption Status | Remark Roof (cone/Floating) | RTL Roof (cone/Floating) | Status PV Vent/Flame Arrester | Caption Status | Remark PV Vent/Flame Arrester | RTL PV Vent/Flame Arrester | Status Tank Heater (electric/steam) | Caption Status | Remark Tank Heater (electric/steam) | RTL Tank Heater (electric/steam) | Status Mixer | Caption Status | Remark Mixer | RTL Mixer | Status Stairway/Handrail/Platform | Caption Status | Remark Stairway/Handrail/Platform | RTL Stairway/Handrail/Platform | Status Annular Plate | Caption Status | Remark Annular Plate | RTL Annular Plate | Status Bottom Plate | Caption Status | Remark Bottom Plate | RTL Bottom Plate | Status Gate Valve in/out | Caption Status | Remark Gate Valve in/out | RTL Gate Valve in/out | Status Foundation | Caption Status | Remark Foundation | RTL Foundation | Status Expansion Joint | Caption Status | Remark Expansion Joint | RTL Expansion Joint | Stataus Roof Drain | Caption Status | Remark Roof Drain | RTL Roof Drain | Status ESV/PSV | Caption Status | Remark ESV/PSV | RTL ESV/PSV | Status MOV | Caption Status | Remark MOV | RTL MOV | Status Rolling Ladder | Caption Status | Remark Rolling Ladder | RTL Rolling Ladder | Status Skirt/Fireproofing | Caption Status | Remark Skirt/Fireproofing | RTL Skirt/Fireproofing | Status Painting | Caption Status | Remark Painting | RTL Painting | Status Roof Seal (Floating Roof) | Caption Status | Remark Roof Seal (Floating Roof) | RTL Roof Seal (Floating Roof) | Month Update
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 140-T-4/00 | Fixed roof | Cracked Slope Tank | Prioritas 3 | Operation | T.475/PTKN.4.5/SKHP/DL/07/2022 | 2025-04-16 | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/140-T-04 | Valid | Valid | 1899-12-31 | 2031-06-01 | Valid | 4291/PKTN/4.5/DL/12/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Reaching the end of lifetime within less than 3 years | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-UTL -550 | 550-TK-701/00 | Fixed roof | Fuel Oil Tank | Prioritas 3 | Operation | No Custody | No Custody | Valid | 2026-07-15 | 009a/E08-L11/P1/2022/550-TK-701 | Valid | Valid | 1899-12-31 | Non- custody | Valid | Non- custody | NA | NA | No Issue | No Issue | Good | Standard | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | NA | NA | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-UTL -920 | 920-T-1/00 | Fixed roof | Fuel Oil Tank | Prioritas 3 | Operation | No Custody | No Custody | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/920-T-01 | Valid | Valid | 1899-12-31 | Non- custody | Valid | Non- custody | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No IssueIndikasi Vapor release; RTL monitoring vapor release dengan gas test | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-UTL -920 | 920-T-2/00 | Fixed roof | Fuel Oil Tank | Prioritas 3 | Operation | No Custody | No Custody | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/920-T-02 | Valid | Valid | 1899-12-31 | Non- custody | Valid | Non- custody | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-01/00 | Fixed roof | Short Residue (DCU Charge) Tank | Prioritas 3 | Overhaul/Cleaning | TU.2264/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-01 | Valid | Valid | 1899-12-31 | I/P Release Sertifikat Tera | Valid | I/P Release Sertifikat Tera | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | RLA course #1 < 5 tahun | OH | Good With Note | Reaching the end of lifetime within less than 3 years | RLA roof < 3 tahun | OH | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-02/00 | Fixed roof | Short Residue (DCU Charge) Tank | Prioritas 3 | Operation | TU.2126/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-02 | Valid | Valid | 1899-12-31 | 2031-01-01 | Valid | 13/PKTN.4.8/KHP/DL/02/2018 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-03/00 | Fixed roof | M/HVGO | Prioritas 3 | Overhaul/Cleaning | TU.2781/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-03 | Valid | Valid | 1899-12-31 | 2034-02-21 | Valid | TU.1034/PKTN.4.5/DL/03/2024 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Roof deformasi ringan | pengecekan kelayakan operasi dan lakukan perbaikan sementara wrapping (jika di butuhkan) | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-04/00 | Fixed roof | M/HVGO | Prioritas 3 | Operation | TU.1734/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-04 | Valid | Valid | 1899-12-31 | 2031-03-01 | Valid | 3133/PKTN.4.8/KHP/DL/09/2021 | Good | All functional | No Issue | No Issue | Good With Note | Standard | Pengunaan Grounding yang SubstandardNo Issue | penambahan/penggantian grounding Material grounding lug menggunakan stainless steel sebanyak 6 pcs dengan jarak maksimal 30 meter. | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Reaching the end of lifetime within less than 3 years |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Deformasi pada roof | Pergantian total roof dan grouting | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-05/00 | Fixed roof | HEAVY NAPHTHA | Prioritas 1 | Operation | TU.2272/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-05 | Valid | Valid | 1899-12-31 | 2033-03-01 | Valid | T 53/PKTN4.5/KHP/DL/03/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-06/00 | Fixed roof | NAPHTHA | Prioritas 1 | Operation | TU.2123/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-06 | Valid | Valid | 1899-12-31 | Bebas Tera Ulang | Valid | 1788/PKTN4.8/KHP/DL/06/2018 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No IssueIndikasi Vapor release dari cont’s seal;RTL Monitoring vapor release dengan gas test | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-07/00 | Floating roof | Light Naphtha | Prioritas 1 | Overhaul/Cleaning | TU.2129/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-07 | Valid | Valid | 1899-12-31 | 2031-04-01 | Valid | 3501/PKTN.4.8/KHP/DL/10/21 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Not Good | Reaching the end of lifetime within less than 3 years | Roof deformasi sehingga ada genangan | wrapping untuk meminimalisir genangan pada roof | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Not Good | Damage causing hydrocarbon release. | Indikasi vapor release pada roof seal | Pengetesan gas flamibility untuk monitoring vapor release | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-08/00 | Fixed roof | Kerosene Tank | Prioritas 2 | Operation | TU.1735/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-08 | Valid | Valid | 1899-12-31 | 2032-09-01 | Valid | TU.3097/PKTN.4.8/DL/10/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-09/00 | Floating roof | AVIGAS-HOMC | Prioritas 1 | Operation | TU.2124/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-09 | Valid | Valid | 1899-12-31 | 2029-02-01 | Valid | 358/PKTN4.8/KHP/DL/02/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional |  |  | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-10/00 | Floating roof | AVIGAS-HOMC | Prioritas 1 | Operation | TU.2267/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | 2028-07-01 | Valid | 854/PKTN4.8/KHP/DL/08/2018 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Damage causing hydrocarbon release. |  |  | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-11/00 | Floating roof | AVIGAS-HOMC | Prioritas 1 | Operation | TU.1736/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-11 | Valid | Valid | 1899-12-31 | 2031-02-01 | Valid | 3511/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-12/00 | Floating roof | Super Mogas (LOMC) Tank | Prioritas 1 | Operation | TU.5408/PKTN.4.5/DL/11/2024 | 2026-10-24 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-12 | Valid | Valid | 1899-12-31 | 2032-01-01 | Valid | 262/PKTN.4.8/KHP/DL/01/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional |  |  | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-13/00 | Floating roof | Premium Tank | Prioritas 1 | Operation | TU.5261/PKTN.4.5/DL/10/2024 | 2026-10-24 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-13 | Valid | Valid | 1899-12-31 | 2032-01-01 | Valid | TU.263/PKTN.4.8/KHP/DL/01/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-14/00 | Floating roof | Super Mogas (LOMC) Tank | Prioritas 1 | Operation | TU.2274/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/945-T-14 | Valid | Valid | 1899-12-31 | 2030-08-01 | Valid | 572/PKTN.4.8/KHP/DL/09/2020 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Not Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Not Good | Damage causing hydrocarbon release. |  |  | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-15/00 | Floating roof | Premium Tank | Prioritas 1 | Overhaul/Cleaning | TU.1737/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-15 | Valid | Valid | 1899-12-31 | 2033-03-01 | Valid | TU.948/PKTN.4.5/KHP/DL/03/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Not Good | Damage causing hydrocarbon release. | Indikasi vapor release pada roof seal | Pengetesan gas flamibility untuk monitoring vapor release | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-16/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | TU.1738/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-16 | Valid | Valid | 1899-12-31 | 2034-02-19 | Valid | TU.1033/PKTN.4.5/DL/03/2024 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-17/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | TU.1739/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/945-T-17 | Valid | Valid | 1899-12-31 | 2031-02-01 | Valid | 3506/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-18/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | TU.1740/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-18 | Valid | Valid | 1899-12-31 | 2034-02-23 | Valid | TU.1036/PKTN.4.5/DL/03/2024 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No IssueIndikasi Vapor release dari cont’s seal; Progres RTL : Monitoring vapor release dengan gas test | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-19/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | TU.1741/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-19 | Valid | Valid | 1899-12-31 | 2031-02-01 | Valid | 1421/PKTN.4.8/KHP/DL/04/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good With Note | Lifetime ≥ 3 years, no damage | Bottom Patching, Temporary Wrapping | Wrapping partial pada bottom plate dengan kualitas dari supplier selama 5 tahun, sehingga RL bottom plate ± 10 tahun | Good | Functional | No Issue | No Issue | Good | No Issue | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-20/00 | Fixed roof | SOLAR | Prioritas 2 | Overhaul/Cleaning | TU.2284/PKTN.4.5/DL/08/2024 | 2026-07-12 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-20 | Valid | Valid | 1899-12-31 | 2033-03-01 | Valid | TU.950/PKTN.4.5/KHP/DL/03/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | RLA Shell Course < 5 year | OH | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | RLA roof < 3 tahun | OH | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-21/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.1742/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-21 | Valid | Valid | 1899-12-31 | 2029-04-01 | Valid | 1326/PKTN.4.8/KHP/DL/04/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good With Note | Lifetime ≥ 3 years, no damage | Wrapping pada roof | Lakukan wrapping untuk mencegah genangan air pada roof | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-22/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.1743/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-22 | Valid | Valid | 1899-12-31 | 2031-06-01 | Valid | 726/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-23/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.1744/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2025-08-10 | 009a/E08-L11/P1/2022/945-T-23 | Valid | Valid | 1899-12-31 | 2031-06-01 | Valid | 3504/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Deformasi pada roof | Lakukan wrapping untuk mencegah genangan air pada roof | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-24/00 | Fixed roof | Heavy Slop | Prioritas 3 | Overhaul/Cleaning | TU.2268/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-24 | Valid | Valid | 1899-12-31 | I/P Release Sertifikat Tera Sept s '26 | Valid | 3503/PKTN/4.8/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | RLA Shell course < Min thickness | OH | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | RLA roof < 3 tahun | OH | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-25/00 | Fixed roof | Light Slop | Prioritas 3 | Operation | TU.2224/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-25 | Valid | Overdue > 3 tahun | 1899-12-31 | 2032-09-01 | Valid | TU.3095/PKTN.4.8/DL/10/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Roof 20% wrapping | OH | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good With Note | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-26/00 | Fixed roof | FLUSHING OIL | Prioritas 3 | Operation | TU.2263/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-26 | Valid | Valid | 1899-12-31 | 2033-09-01 | Valid | TU.3313/PKTN.4.5/KHP/DL/09/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | RLA Shell course < 5 tahun | OH | Good With Note | Reaching the end of lifetime within less than 3 years | Deformasi pada roof | Pergantian total roof dan grouting | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -LPG | 945-T-27/00 | Spherical Tank | LPG Sphere Tank | Prioritas 1 | Operation | TU.5619/PKTN.4.5/DL/07/2025 | 2027-07-03 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-27 | Valid | Valid | 1899-12-31 | 2029-01-01 | Valid | 122/PKTN.4.8/KHP/DL/02/2017 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Cracked at support columns over ≤50% | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-28/00 | Floating roof | Premium Tank | Prioritas 1 | Operation | TU.1745/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | 2032-11-01 | Valid | TU.4293/PKTN.4.5/DL/12/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-29/00 | Floating roof | Premium Tank | Prioritas 1 | Operation | TU.1746/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-29 | Valid | Valid | 1899-12-31 | 2030-11-01 | Valid | 948/PKTN.4.8/KHP/DL/12/2020 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Damage causing hydrocarbon release. | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -LPG | 945-T-30/00 | Spherical Tank | LPG Sphere Tank | Prioritas 1 | Operation | TU.2285/PKTN.4.5/DL/08/2024 | 2026-07-12 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-30 | Valid | Overdue < 3 tahun | 1899-12-31 | 2029-06-01 | Valid | 2154/PKTN.4.8/KHP/DL/06/2017 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Cracked at support columns over ≤50% | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | 945-T-301/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.1748/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | ALAFAP | Valid | Overdue < 3 tahun | 1899-12-31 | 2032-09-01 | Valid | TU.3093/PKTN.4.8/DL/10/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -LPG | 945-T-31/00 | Spherical Tank | LPG Sphere Tank | Prioritas 1 | Operation | TU.1747/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-31 | Valid | Overdue < 3 tahun | 1899-12-31 | 2029-06-01 | Valid | 2153/PKTN.4.8/KHP/DL/06/2017 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No IssueNo IssueIndikasi Vapor release; RTL monitoring vapor release dengan gas test | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Cracked at support columns over ≤50% | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -LPG | 945-T-32/00 | Spherical Tank | LPG Sphere Tank | Prioritas 1 | Overhaul/Cleaning | TU.5620/PKTN.4.5/DL/07/2025 | 2027-07-03 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-32 | Valid | Valid | 1899-12-31 | 2029-06-01 | Valid | 2152/PKTN.4.8/KHP/DL/06/2017 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Shell Thickness minimum > actual thickness | lakukan pergantian total shell, Mitigasi sementara ReNo IssueRating | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Cracked at support columns over ≤50% | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -LPG | 945-T-33/00 | Spherical Tank | LPG Sphere Tank | Prioritas 1 | Operation | TU.2786/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/945-T-33 | Valid | Valid | 1899-12-31 | 2029-06-01 | Valid | 2155/PKTN.4.8/KHP/DL/06/2017 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Cracked at support columns over ≤50% | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-34/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.2775/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | 2029-01-01 | Valid | 356/PKTN.4.8/KHP/DL/02/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Shell course #1 thickness actual < minimum thickness | ReNo IssueRating | Good With Note | Damage causing hydrocarbon release; reaching retiring thickness | Roof berlubang | Lakukan wrapping untuk mencegah genangan air pada roof | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | 945-T-35/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.2266/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | 2031-02-01 | Valid | 3509/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Shell course #1 thickness actual < minimum thickness | ReNo IssueRating | Good With Note | Reaching the end of lifetime within less than 3 years | Deformasi pada roof | Lakukan wrapping untuk mencegah genangan air pada roof | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -SSD | DB-TK-1A/00 | Fixed roof | BALLAST | Prioritas 3 | Operation | TU.2125/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2026-11-18 | /ALAFAM | Valid | Overdue > 3 tahun | 1899-12-31 | 2032-06-01 | Valid | 2177/PKTN.4.8/DL/08/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Roof plate mengalami deformasi | OH | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good With Note | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -SSD | DB-TK-1B/00 | Fixed roof | BALLAST | Prioritas 3 | Overhaul/Cleaning | TU.2286/PKTN.4.5/DL/08/2024 | 2026-07-12 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | 2029-09-01 | Valid | 4056/PKTN.4.8/KHP/DL/11/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | Roof plate mengalami deformasi berat | pemberhentian operasi karena resiko hydrocarbon release dan lakukan penggantian roof plate | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TCR | TK-101/00 | Fixed roof | Mix Crude Oil | Prioritas 1 | Overhaul/Cleaning | TU.2779/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | I/P Release Sertifikat Tera Sept s '26 | Valid | 1419/PKTN.4.8/KHP/DL/04/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | RLA roof < 3 tahun | OH | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TCR | TK-102/00 | Fixed roof | Mix Crude Oil | Prioritas 1 | Operation | TU.1749/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-102 | Valid | Valid | 1899-12-31 | 2032-06-01 | Valid | 2174/PKTN.4.8/DL/08/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TCR | TK-103/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.1750/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-103 | Valid | Overdue > 3 tahun | 1899-12-31 | 2032-06-01 | Valid | 2178/PKTN.4.8/DL/08/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | buckling course #7 dan #8 | OH | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | RLA roof < 3 tahun | OH | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Not Good | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TCR | TK-104/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.1751/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | 2028-07-01 | Valid | 853/PKTN.4.8/KHP/DL/08/2018 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | RLA Shell course #1 < 5 tahun | OH | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional |  |  | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TCR | TK-105/00 | Fixed roof | DCO/FO | Prioritas 1 | Operation | TU.1752/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | 2032-01-01 | Valid | 265/PKTN.4.8/KHP/DL/01/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TCR | TK-106/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.2287/PKTN.4.5/DL/08/2024 | 2026-07-12 | Valid | 2026-11-18 | ALAFAP | Valid | Valid | 1899-12-31 | 2030-08-01 | Valid | 573/PKTN.4.8/KHP/DL/09/2020 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional |  |  | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TCR | TK-107/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.1753/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | /ALAFAM | Valid | Overdue < 3 tahun | 1899-12-31 | 2031-03-01 | Valid | 3137/PKTN.4.8/KHP/DL/09/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Over 40% corrosion on primer layer | Coating pada roof mengalami blistering dan chalking | Recoating | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-201/00 | Fixed roof | Heavy Slop | Prioritas 3 | Operation | TU.2282/PKTN.4.5/DL/08/2024 | 2026-07-12 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | Mei 2031 | Valid | T.4162/PKTN.4.5/DL/06/2025 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | RLA roof < 3 tahun |  | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-202/00 | Floating roof | Light Slop | Prioritas 3 | Operation | TU.2127/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-202 | Valid | Overdue > 3 tahun | 1899-12-31 | 2028-07-01 | Valid | 771/PKTN.4.8/DL/08/2018 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Not Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good With Note | Exceeding 50% from standard; settlement between D/50 and D/100 | Pondasi berongga | injeksi concreate | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Not Good | Damage causing hydrocarbon release. | Indikasi vapor release pada roof seal | Pengetesan gas flamibility untuk monitoring vapor release | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-203/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Overhaul/Cleaning | TU.2782/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-203 | Valid | Valid | 1899-12-31 | 2031-08-01 | Valid | 3513/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | RLA Shell course #1 < 5 tahun | OH | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional |  | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-204/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.1754/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-204 | Valid | Valid | 1899-12-31 | 2031-04-01 | Valid | 723/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-205/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.1755/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2030-08-10 | 009a/E08-L11/P1/2022/610-TK-205 | Valid | Valid | 1899-12-31 | 2031-03-01 | Valid | 1920/PKTN.4.8/KHP/DL/05/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-206/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.2262/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-206 | Valid | Valid | 1899-12-31 | 2032-01-01 | Valid | 266/PKTN.4.8/KHP/DL/01/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-207/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.2269/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | ASAAAL/PMU-KP | Valid | Valid | 1899-12-31 | 2033-03-01 | Valid | T.54/PKTN.4.5/KHP/DL/03/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-208/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | TU.2778/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/610-TK-208 | Valid | Valid | 1899-12-31 | 2032-06-01 | Valid | 2179/PKTN.4.8/DL/08/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-209/00 | Fixed roof | Kerosene Tank | Prioritas 2 | Overhaul/Cleaning | TU.2784/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/610-TK-209 | Valid | Valid | 1899-12-31 | 2033-03-01 | Valid | TU.949/PKTN.4.5/KHP/DL/03/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Reaching the end of lifetime within less than 3 years | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-210/00 | Fixed roof | Kerosene Tank | Prioritas 2 | Operation | TU.1756/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2025-08-10 | 009a/E08-L11/P1/2022/610-TK-210 | Valid | Valid | 1899-12-31 | 2031-03-01 | Valid | 3135/PKTN.4.8/KHP/DL/09/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-211/00 | Fixed roof | Fuel Oil Tank | Prioritas 3 | Operation | TU.2273/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-211 | Valid | Valid | 1899-12-31 | 2032-04-01 | Valid | T310/PKTN.4.8/DL/04/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-212/00 | Fixed roof | Fuel Oil Tank | Prioritas 3 | Operation | TU.2265/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-212 | Valid | Valid | 1899-12-31 | 2032-11-01 | Valid | TU.4292/PKTN.4.5/DL/12/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-213/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.2275/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2025-08-10 | ALAFAP | Valid | Valid | 1899-12-31 | 2031-04-01 | Valid | 724/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue temporary Wrapping, I/P tender | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-214/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.5407/PKTN.4.5/DL/11/2024 | 2026-10-24 | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/610-TK-214 | Valid | Valid | 1899-12-31 | 2032-06-01 | Valid | 2175/PKTN.4.8/DL/08/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Shell course #1 thickness actual < minimum thickness | Spot wrapping shell #1 indikasi thinning | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-215/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.1757/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-215 | Valid | Valid | 1899-12-31 | 2029-09-01 | Valid | 4247/PKTN.4.8/KHP/DL/11/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-216/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.5409/PKTN.4.5/DL/11/2024 | 2026-10-24 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-216 | Valid | Valid | 1899-12-31 | 2033-03-01 | Valid | TU.946/PKTN.4.5/KHP/DL/03/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-217/00 | Floating roof | AVIGAS-HOMC | Prioritas 1 | Operation | TU.1758/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-217 | Valid | Overdue < 3 tahun | 1899-12-31 | 2031-08-01 | Valid | 3512/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | RLA Shell course #1 < 5 tahun | OH | Not Good | Reaching the end of lifetime within less than 3 years | roof deformasi ringan | Lakukan wrapping untuk menhindari genangan air pada roof | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Not Good | Damage causing hydrocarbon release. | Indikasi vapor release pada roof seal | Pengetesan gas flamibility untuk monitoring vapor release | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-218/00 | Floating roof | NAPHTHA | Prioritas 1 | Overhaul/Cleaning | I/p (Tanki baru) | I/p (Tanki baru) | I/p (Tanki baru) | I/p (Tanki baru) | I/p (Tanki baru) | I/p (Tanki baru) | I/p (Tanki baru) | 1899-12-31 | I/p (Tanki baru) | I/p (Tanki baru) | I/p (Tanki baru) | Good | All functional | I/p (Tanki baru) | I/p (Tanki baru) | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage |  | OH | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion |  |  | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-219/00 | Floating roof | NAPHTHA | Prioritas 1 | Operation | TU.1759/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-219 | Valid | Valid | 1899-12-31 | 2033-03-01 | Valid | TU.947/PKTN.4.5/KHP/DL/03/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage |  | OH | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion |  |  | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-220/00 | Floating roof | AVIGAS-HOMC | Prioritas 1 | Operation | TU.2777/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2027-07-24 | 12005-02-ENI/31K/E08-L11/PI/2023 | Valid | Valid | 1899-12-31 | 2032-09-01 | Valid | TU.3096/PKTN.4.8/DL/10/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Not Good | Reaching the end of lifetime within less than 3 years | roof deformasi ringan | Lakukan wrapping untuk menhindari genangan air pada roof | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Not Good | Damage causing hydrocarbon release. | Indikasi vapor release pada roof seal | Pengetesan gas flamibility untuk monitoring vapor release | 2026-07-27
RU II Dumai | RU02-HSC | 100-CRUDE-HEAT | TK-221/00 | Fixed roof | Fuel Oil Tank | Prioritas 3 | Operation | No Custody | No Custody | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-221 | Valid | Valid | 1899-12-31 | Non- custody | Valid | Non- custody | Good | NA | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | NonNo Issuefunctional | No Issue | No Issue | Good | Exceeding 50% from standard; settlement between D/50 and D/100 | Pondasi berongga | injeksi concreate | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Cracked at support columns over ≤50% | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-222/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.1760/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | 2034-02-20 | Valid | TU.1035/PKTN.4.5/DL/03/2024 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | RLA course #1 dan #5 < Min thickness | OH | Good With Note | Damage causing hydrocarbon release; reaching retiring thickness | Roof sudah di wrapping, terdapat titik yang Kembali berlubang | Pergantian total roof plate dan pergantian Shell course #1 dan #5 | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-223/00 | Fixed roof | LSWR | Prioritas 3 | Overhaul/Cleaning | TU.2788/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/610-TK-223 | Valid | Valid | 1899-12-31 | 2031-11-01 | Valid | 2151/PKTN.4.8/KHP/DL/6/2017 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | Shell 1No Issue5 thickness remaining < 1 tahun | No Issue Mitigasi sementara: rerating level tangki No Issue pergantian total shell saat dilakukan OH | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | 70% roof sudah dilakukan wrapping | No IssueMitigasi sementara: wrapping pada area yang thinning/berlubang 'No Issue Pergantian total roof | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | NA | NA | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-224/00 | Fixed roof | Kerosene Tank | Prioritas 2 | Overhaul/Cleaning | TU.1761/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | ALAFAP | Valid | Valid | 1899-12-31 | 2033-03-01 | Valid | TU.951/PKTN.4.5/KHP/DL/03/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Shell course #1 thickness actual < minimum thickness | ReNo IssueRating | Good With Note | Reaching the end of lifetime within less than 3 years | Deformasi pada roof sudah di wrapping | OH | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-225/00 | Floating roof | NAPHTHA | Prioritas 1 | Operation | TU.2776/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | /ALAFAM | Valid | Valid | 1899-12-31 | 2032-09-01 | Valid | TU.3094/PKTN.4.8/DL/10/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Not Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | Good | Good | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Not Good | Damage causing hydrocarbon release. | Indikasi vapor release pada roof seal | Pengetesan gas flamibility untuk monitoring vapor release | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-226/00 | Fixed roof | Flux Oil | Prioritas 3 | Operation | TU.2270/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-226 | Valid | Valid | 1899-12-31 | 2030-08-01 | Valid | 574/PKTN.4.8/KHP/DL/09/2020 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Roof wrapping karena thinning | Pergantian total roof dan grouting | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good With Note | Exceeding 50% from standard; settlement between D/50 and D/100 | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-227/00 | Fixed roof | Fuel Oil Tank | Prioritas 3 | Operation | TU.2271/PKTN.4.5/DL/02/2026 | 2028-02-08 | Valid | 2027-07-24 | 12008-02-ENI/31K/E08-L11/PI/2023 | Valid | Valid | 1899-12-31 | 2028-07-01 | Valid | 770/PKTN.4.8/KHP/DL/08/2018 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No IssueNo IssueIndikasi Vapor release; RTL monitoring vapor release dengan gas test | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-228/00 | Fixed roof | Flux Oil | Prioritas 3 | Operation | TU.2780/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/610-TK-228 | Valid | Valid | 1899-12-31 | 2032-01-01 | Valid | 264/PKTN.4.8/KHP/DL/01/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Shell course #5 buckling | OH | Good With Note | Reaching the end of lifetime within less than 3 years | Deformasi pada roof | Pergantian total roof dan grouting | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-229/00 | Fixed roof | Flux Oil | Prioritas 3 | Operation | TU.2783/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-229 | Valid | Valid | 1899-12-31 | 2032-06-01 | Valid | 2176/PKTN.4.8/DL/08/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Deformasi pada roof | Pergantian total roof dan grouting | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-230/00 | Fixed roof | Marine Diesel Fuel Tank | Prioritas 3 | Operation | TU.1762/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2025-08-10 | 009a/E08-L11/P1/2022/610-TK-230 | Valid | Valid | 1899-12-31 | 2031-02-01 | Valid | 3510/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Deformasi pada roof | Pergantian total roof dan grouting | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-231/00 | Fixed roof | Marine Fuel Oil | Prioritas 3 | Operation | TU.1763/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/610-TK-231 | Valid | Valid | 1899-12-31 | 2031-03-01 | Valid | 3134/PKTN.4.8/KHP/DL/09/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TPR | TK-232/00 | Fixed roof | Marine Fuel Oil | Prioritas 3 | Operation | TU.1667/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/610-TK-232 | Valid | Valid | 1899-12-31 | 2031-06-01 | Valid | 3505/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Deformasi pada roof | Pergantian total roof dan grouting | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TK-233/00 | Fixed roof | M/HVGO | Prioritas 3 | Operation | TU.1668/PKTN.4.5/DL/03/2025 | 2027-02-16 | Valid | 2026-11-18 | 046-02-SBC/009a/E08-L11/P1/2022/610-TK-233 | Valid | Valid | 1899-12-31 | 2031-06-01 | Valid | 725/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | Shell course #2 dan course #3 pada sisi bagian barat mengalami deformasi | pengecekan kelayakan operasi | Good With Note | Reaching the end of lifetime within less than 3 years | Deformasi pada roof | Pergantian total roof dan grouting | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TY-TK-01/00 | Floating roof | SR- Naptha | Prioritas 1 | Operation | TU.2121/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/TY-TK-1 | Valid | Valid | 1899-12-31 | 2032-01-01 | Valid | TU.267/PKTN.4.8/KHP/DL/01/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage |  | OH | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TY-TK-03/00 | Floating roof | AVIGAS-HOMC | Prioritas 1 | Overhaul/Cleaning | TU.2120/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2027-07-24 | 12015-02-ENI/31K/E08-L11/PI/2023 | Valid | Valid | 1899-12-31 | 2031-02-01 | Valid | 3508/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Not Good / Good With Note |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TY-TK-04/00 | Floating roof | AVIGAS-HOMC | Prioritas 1 | Operation | TU.2119/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2027-07-24 | 12016-02-ENI/31K/E08-L11/PI/2023 | Valid | Valid | 1899-12-31 | 2029-09-01 | Valid | 1461/PKTN.4.8/KHP/DL/11/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Good | Functional | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TY-TK-05/00 | Floating roof | NAPHTHA | Prioritas 1 | Overhaul/Cleaning | TU.2787/PKTN.4.5/DL/03/2025 | 2027-03-14 | Valid | 2027-07-24 | 12017-02-ENI/31K/E08-L11/PI/2023 | Valid | Valid | 1899-12-31 | 2031-02-01 | Valid | 3507/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Operational | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | Not Good | Damage causing hydrocarbon release. | Indikasi vapor release pada roof seal | Pengetesan gas flamibility untuk monitoring vapor release | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TY-TK-2A/00 | Fixed roof | SR- Naptha | Prioritas 1 | Overhaul/Cleaning | TU.2120/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/TY-TK-2 A | Valid | Valid | 1899-12-31 | 2031-06-01 | Valid | 3503/PKTN/4.8/DL/10/2021 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | RLA Shell Course #4 < 5 year | OH | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-ITP | RU02-ITP -TIT | TY-TK-2B/00 | Fixed roof | SR- Naptha | Prioritas 1 | Operation | TU.2122/PKTN.4.5/DL/02/2026 | 2028-02-15 | Valid | 2026-11-18 | 009a/E08-L11/P1/2022/TY-TK-2 B | Valid | Valid | 1899-12-31 | 2032-11-01 | Valid | 4290/PKTN4.5/KHP/DL/12/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Reaching the end of lifetime within less than 3 years | RLA Shell Course #1 dan #2 < 5 year | OH | Good | Lifetime ≥ 3 years, no damage |  | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | Good | Operational | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue | No Issue | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -CDU | 101-TK-16/00 | Fixed roof | DCO/FO | Prioritas 3 | Operation | No Custody | No Custody | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-1 | Valid | Valid | 1899-12-31 | 2029-08-01 | Valid | 2303/PKTN.4.8/KHP/DL/08/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -CDU | 101-TK-16A/00 | Fixed roof | DCO/FO | Prioritas 3 | Operation | No Custody | No Custody | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-2 | Valid | Valid | 1899-12-31 | 2030-03-01 | Valid | 958/PKTN.4.8/KHP/DL/03/2020 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-01/00 | Fixed roof | Kerosene | Prioritas 2 | Operation | TU.4235/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-3 | Valid | Valid | 1899-12-31 | 2033-05-01 | Valid | TU.1768/PKTN.4.5/KHP/DL/06/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-02/00 | Fixed roof | Kerosene | Prioritas 2 | Operation | TU.4236/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-4 | Valid | Valid | 1899-12-31 | 2033-05-01 | Valid | TU.1770/PKTN.4.5/KHP/DL/06/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-03/00 | Fixed roof | Kerosene | Prioritas 2 | Operation | TU.4664/PKTN.4.5/DL/06/2025 | 2027-06-20 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-5 | Valid | Valid | 1899-12-31 | 2032-04-01 | Valid | TU.1888/PKTN.4.8/KHP/DL/5/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-05/00 | Fixed roof | NAPHTHA | Prioritas 1 | Overhaul/Cleaning | TU.4237/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-6 | Valid | Valid | 1899-12-31 | 2029-04-01 | Valid | 1333/PKTN.4.8./KHP/DL/04/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-06/00 | Fixed roof | Kerosene | Prioritas 2 | Operation | TU.4665/PKTN.4.5/DL/06/2025 | 2027-06-20 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-7 | Valid | Valid | 1899-12-31 | 2030-03-01 | Valid | 957/PKTN.4.8/KHP/DL/03/2020 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-07/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.4666/PKTN.4.5/DL/06/2025 | 2027-06-20 | Valid | 2023-03-01 | 104-02-PRC/104/E08-L03/P1/2021-8 | Valid | Valid | 1899-12-31 | 2032-04-01 | Valid | TU.1787/PKTN.4.8/KHP/DL/5/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-08/00 | Fixed roof | LSWR | Prioritas 3 | Overhaul/Cleaning | TU.4667/PKTN.4.5/DL/06/2025 | 2027-06-20 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-9 | Valid | Valid | 1899-12-31 | 2028-09-01 | Valid | 3070/PKTN.4.8/KHP/DL/10/2018 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-09/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.4131/PKTN.4.5/DL/06/2025 | 2027-05-25 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-10 | Valid | Overdue < 3 tahun | 1899-12-31 | 2029-04-01 | Valid | 1329/PKTN.4.8./KHP/DL/04/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-10/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.4239/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-11 | Valid | Valid | 1899-12-31 | 2032-04-01 | Valid | 1785/PKTN.4.8/KHP/DL/05/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-11/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.4241/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-12 | Valid | Overdue < 3 tahun | 1899-12-31 | 2033-05-01 | Valid | TU.1771/PKTN.4.5/KHP/DL/06/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-12/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.4242/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-13 | Valid | Valid | 1899-12-31 | 2029-04-01 | Valid | TU.588/PKTN.4.5/KHP/DL/02/2024 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Lifetime ≥ 3 years, no damage | Shell Thinning | OH | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | Rembesan pada bottom tangki | Telah dilakukan Patching bottom tangki tangki bocor kembali, mitigasi dengan melakukan monitoring dan OH | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-13/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.4243/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-14 | Valid | Valid | 1899-12-31 | 2030-10-01 | Valid | TU.5285/PKTN.4.5/DL/11/2024 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-14/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.4245/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-15 | Valid | Overdue < 3 tahun | 1899-12-31 | 2030-03-01 | Valid | 956/PKTN.4.8/KHP/DL/03/2020 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-15/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Overhaul/Cleaning | TU.4244/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-16 | Valid | Valid | 1899-12-31 | 2029-04-01 | Valid | 1331/PKTN.4.8./KHP/DL/04/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-16/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.4240/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-17 | Valid | Overdue < 3 tahun | 1899-12-31 | 2032-04-01 | Valid | TU.587/PKTN.4.5/KHP/DL/02/2024 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-17/00 | Fixed roof | CRUDE OIL | Prioritas 3 | Overhaul/Cleaning | TU.4246/PKTN.4.5/DL/05/2026 | 2028-05-02 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-18 | Valid | Valid | 1899-12-31 | 2009-04-01 | Expired | 109/PDN.4.3.2/S/IV/2003 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good With Note | Exceeding 50% from standard; settlement between D/50 and D/100 |  |  | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good With Note | Over 40% corrosion on primer layer |  |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-18/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.4669/PKTN.4.5/DL/06/2025 | 2027-06-20 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-19 | Valid | Overdue < 3 tahun | 1899-12-31 | 2032-04-01 | Valid | 1789/PKTN.4.8/KHP/DL/5/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-19/00 | Fixed roof | Kerosene | Prioritas 2 | Overhaul/Cleaning | TU.4668/PKTN.4.5/DL/06/2025 | 2027-06-20 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-20 | Valid | Valid | 1899-12-31 | 2030-03-01 | Valid | 955/PKTN.4.8/KHP/DL/03/2020 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Not Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-20/00 | Fixed roof | Kerosene | Prioritas 2 | Operation | TU.4670/PKTN.4.5/DL/06/2025 | 2027-06-20 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-21 | Valid | Valid | 1899-12-31 | 2033-05-01 | Valid | TU.1769/PKTN.4.5/KHP/DL/06/2023 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-21/00 | Fixed roof | Kerosene | Prioritas 2 | Operation | TU.4671/PKTN.4.5/DL/06/2025 | 2027-06-20 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-22 | Valid | Valid | 1899-12-31 | 2034-01-01 | Valid | TU.589/PKTN.4.5/KHP/DL/02/2024 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-22/00 | Fixed roof | NAPHTHA | Prioritas 1 | Operation | TU.4673/PKTN.4.5/DL/06/2025 | 2027-06-20 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-23 | Valid | Valid | 1899-12-31 | 2029-08-01 | Valid | 906/PKTN.4.8/KHP/DL/08/2019 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU II Dumai | RU02-SPK | RU02-SPK -ITY | 946-TK-23/00 | Fixed roof | SOLAR | Prioritas 2 | Overhaul/Cleaning | TU.4672/PKTN.4.5/DL/06/2025 | 2027-06-20 | Valid | 2025-07-01 | 104-02-PRC/104/E08-L03/P1/2021-24 | Valid | Valid | 1899-12-31 | 2032-04-01 | Valid | 1786/PKTN.4.8/KHP/DL/5/2022 | Good | All functional | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Standard | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Lifetime ≥ 3 years, no damage | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good | No Issue | No Issue | Good | Lifetimhhhhte ≥ 3 years, no damage | No Issue | No Issue | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional | No Issue | No Issue | Good | <25% from standard, no significant settlement | No Issue | No Issue | Good | Properly aligned and in good condition | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Functional | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | NA | NA | No Issue | No Issue | Good | Good, no significant corrosion | No Issue |  | NA | NA | No Issue | No Issue | 2026-07-27
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-001/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.014.22 | Valid | Overdue > 3 tahun |  | 15 Juli 2033 | Valid | TU.2817/PKTN.4.5/KHP/DL/08/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-002/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Overhaul/Cleaning | [6 empty] | Valid | [132 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-003/00 | Fixed roof | Avtur Tank | Prioritas 2 | Overhaul/Cleaning |  |  | Valid | 2026-09-20 | P009.NH.SA.016.22 | Valid | Valid |  | 09 Mei 2028 | Valid | 3058/PKTN.4.8/KHP/DL/10/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-004/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | T.0076/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.017.22 | Valid | Valid |  | 10 Mei 2028 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-005/00 | Fixed roof | Naphtha Intermedia | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.018.22 | Valid | Valid |  | 26 Mei 2032 | Valid | T.449/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-006/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | T.0077/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.019.22 | Valid | Valid |  | 30 Mei 2032 | Valid | T.446/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-007/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | T.0063/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2022-09-27 | Fixed roof | Valid | Valid |  | 21 Maret 2033 | Valid | T.56/PKTN.4.5/KHP/DL/04/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-008/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.021.22 | Valid | Valid |  | 10 Mei 2034 | Valid | T.93/PKTN.4.8/KHP/DL/08/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-009/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2022-09-27 | 5010-02-ENI/197/E08-L11/P1/2018 | Valid | Valid |  | 26 Januari 2033 | Valid | T.11/PKTN.4.5/DL/02/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-010/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | Fixed roof | Valid | Valid |  | 19 Maret 2032 | Valid | T.268/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-011/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | Fixed roof | Valid | Valid |  | 26 Maret 2034 | Valid | T.75/PKTN.4.5/KHP/DL/04/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-012/00 | Fixed roof | LAWS | Prioritas 3 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.025.22 | Valid | Valid |  | 24 Agustus 2032 | Valid | TU.3082/PKTN.4.8/KHP/DL/10/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-013/00 | Fixed roof | Avtur Tank | Prioritas 3 | Operation | TU.436/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.026.22 | Valid | Valid |  | 29 Agustus 2028 | Valid |  | good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Not Good / Good With Note |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-015/00 | Fixed roof | Avtur Tank | Prioritas 3 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.028.22 | Valid | Valid |  | 1933-11-29 | Valid | TU.445/PKTN.4.5/SKHP/DL/02/2023 | [8 empty] | NA | NA | [14 empty] | NA | NA | [14 empty] | NA | NA | [10 empty] | NA | NA | [18 empty] | NA | NA | [22 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | [6 empty] | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-017/00 | Fixed roof | LAWS | Prioritas 3 | Overhaul/Cleaning |  |  | Valid | 2026-09-20 | P009.NH.SA.030.22 | Valid | Valid |  | 24 Agustus 2032 | Valid | T.3083/PKTN.4.8/KHP/DL/10/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-018/00 | Fixed roof | LAWS | Prioritas 3 | Operation | TU.420/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.031.22 | Valid | Valid |  | 1933-11-23 | Valid | 446/SPKTN.4.5/SKHP/DL/02/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-019/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | TU.419/PKTN.4.5/SKHP/DL/02/2023 |  | Valid |  | 5020-02-ENI/197/E08-L11/P1/2018 | Valid | Valid |  | 16 Desember 2032 | Valid | T.636/PKTN.4.5/KHP/DL/12/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-020/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation |  |  | Valid |  |  | Valid | Valid |  |  | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-021/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation |  |  | Valid | 2026-09-20 | P009.NH.SA.034.22 | Valid | Valid |  |  | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-022/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid |  | 5023-02-ENI/197/E08-L11/P1/2018 | Valid | Valid |  | 21 Oktober 2032 | Valid | T.615/PKTN.4.8/KHP/DL/11/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-023/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.036.22 | Valid | Valid |  | 03 Juli 2028 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-A-024/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | Fixed roof | Valid | Valid |  | 07 Juli 2031 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-B-001/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 3 | Overhaul/Cleaning | NA | 01 Januari 2030 |  | 2026-09-20 | P009.NH.SA.269.22 |  | Valid |  | 1930-09-01 | [10 empty] | NA | NA | [14 empty] | NA | NA | [14 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | [14 empty] | NA | NA |  |  | NA | NA | [6 empty] | NA | NA |  |  | NA | NA | [10 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | [10 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-B-003/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 2 | Overhaul/Cleaning | Idle | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.039.22 |  | Valid |  | 1933-11-17 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-B-004/00 | Fixed roof | PERTALITE | Prioritas 3 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.270.22 |  | Valid |  | 26 Maret 2034 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-B-008/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | Idle | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.040.22 | Valid | Valid |  | 28 Maret 2034 | Valid | TU.1441/PKTN.4.5/KHP/DL/04/2024 | Good | All functional | Idle |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-B-061/00 | Fixed roof | PERTALITE | Prioritas 1 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.041.22 | Valid | Valid |  | 28 Maret 2034 | Valid | TU.1440/PKTN.4.5/KHP/DL/04/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-B-064/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | T.0079/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.042.22 | Valid | Valid |  | 28 Maret 2034 | Valid | TU.1446/PKTN.4.5/KHP/DL/04/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-B-066/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | TU.379/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.043.22 | Valid | Valid |  | 1931-04-02 | Valid | 1489/PKTN.4.8/KHP/DL/04/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-B-067/00 | Fixed roof | Avtur Tank | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.043.22 | Valid | Valid |  | 09 Maret 2024 | Valid |  | good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-B-069/00 | Fixed roof | Avtur Tank | Prioritas 1 | Operation | TU.378/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.045.22 | Valid | Valid |  | 23 Januari 2031 | Valid | 143/PKTN.4.8/KHP/DL/02/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-001/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | TU.390/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.046.22 | Valid | Valid |  | 14 Juli 2033 | Valid | TU.2814/PKTN.4.5/KHP/DL/08/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-002/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Overhaul/Cleaning |  |  | Valid |  |  | Valid | Valid |  |  | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-003/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.048.22 | Valid | Valid |  | 11 Juli 2031 | Valid | 2608/PKTN.4.8/KHP/DL/07/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-004/00 | Fixed roof | Dexlite | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.049.22 | Valid | Valid |  | 20 Maret 2033 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-005/00 | Fixed roof | Dexlite | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.050.22 | Valid | Valid |  | 04 Februari 2034 | Valid | T.22/PKTN.4.5/KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-006/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | TU.391/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.051.22 | Valid | Valid |  | 14 Januari 2029 | Valid | 164/PKTN.4.8/S/DL/02/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-007/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2023-11-07 | 029-10-PBC/1000035764/E08-L11/P8/2022 | Valid | Valid |  | 15 Februari 2029 | Valid | 860/PKTN.4.8/KHP/DL/03/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-008/00 | Fixed roof | BIO FAME | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 07 Mei 2024 | Fixed roof | Valid | Valid |  | 12 Oktober 2029 | Valid | 3625/PKTN.4.8/KHP/DL/10/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-009/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.052.22 | Valid | Valid |  |  | Valid | TU.2003/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-010/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.053.22 | Valid | Valid |  | 19 Mei 2032 | Valid | TU.2004/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-011/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | T.0080/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-04-07 | 029-09-PBC/1000035764/E08-L11/P8/2022 | Valid | Valid |  | 10 Maret 2032 | Valid | T.267/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-012/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | TU.412/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.054.22 | Valid | Valid |  | 22 Januari 2030 | Valid | 83/PKTN.4.8/KHP/DL/2/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-013/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | TU.402/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.055.22 | Valid | Valid |  | 11 Januari 2029 | Valid | 163/PKTN.4.8/S/DL/02/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-D-014/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | TU.387/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.056.22 | Valid | Valid |  | 1930-09-13 | Valid | 614/PKTN.4.8/KHP/DL/09/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-001/00 | Fixed roof | Slop Oil | Prioritas 2 | Idle | TU.376/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 |  | 2026-09-20 | P009.NH.SA.057.22 |  |  |  | 2029-09-29 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-002/00 | Fixed roof | Slop Oil | Prioritas 2 | Idle | TU.383/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 |  | 2026-09-20 | P009.NH.SA.058.22 |  |  |  | 11 Agustus 2028 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-003/00 | Fixed roof | Slop Oil | Prioritas 2 | Idle | TU.417/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 |  | 2026-09-20 | P009.NH.SA.059.22 |  |  |  | 26 Agustus 2032 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-004/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | TU.438/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.060.22 | Valid | Valid |  | 03 Februari 2034 | Valid | T.21/PKTN.4.5/KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-005/00 | Fixed roof | Crude Oil Mixed 3 | Prioritas 2 | Idle | NA | 01 Januari 2030 |  | 2022-09-27 | 5049-02-ENI/197/E08-L11/P1/2018 |  |  |  | 16 Desember 2032 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-007/00 | Fixed roof | Naphtha Intermedia | Prioritas 2 | Operation |  | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.272.22 | Valid | Valid |  | 2024-04-24 | Valid | 530/PKTN.4.8/KHP/DL/06/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-008/00 | Fixed roof | Naphtha Intermedia | Prioritas 2 | Overhaul/Cleaning | TU.421/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.062.22 |  | Valid |  | 10 Januari 2029 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-009/00 | Fixed roof | Slop Oil | Prioritas 2 | Idle | TU.372/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 |  | 2026-09-20 | P009.NH.SA.273.22 |  |  |  | 2024-04-19 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-010/00 | Fixed roof | Crude Oil Mixed 3 | Prioritas 2 | Idle | T.0064/PKTN.4.8/KN/07/2022 | 14 Juli 2024 |  | 2026-09-20 | P009.NH.SA.063.22 |  |  |  | 21 Maret 2024 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-011/00 | Fixed roof | Crude Oil Mixed 2 | Prioritas 1 | Operation | TU.405/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.064.22 | Valid | Valid |  | 21 Maret 2029 | Valid | 465/PKTN.4.8/KHP/DL/04/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-012/00 | Fixed roof | Crude Oil Mixed 2 | Prioritas 1 | Operation | TU.418/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.065.22 | Valid | Valid |  | 21 Oktober 2032 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-E-013/00 | Fixed roof | LONG RESIDUE | Prioritas 1 | Overhaul/Cleaning |  |  | Valid | 2026-09-20 | P009.NH.SA.066.22 | Valid | Valid |  | 13 Maret 2029 | Valid | 1309/PKTN.4.8/KHP/DL/04/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-001/00 | Fixed roof | FLUSHING OIL | Prioritas 2 | Operation | TU.369/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.067.22 | Valid | Valid |  | 23 Maret 2024 | Valid | 1013/PKTN.4.8/KHP/DL/04 /2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Non-functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-002/00 | Fixed roof | FLUSHING OIL | Prioritas 2 | Overhaul/Cleaning |  |  | Valid |  |  | Valid | Valid |  | 21 Maret 2032 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-003/00 | Fixed roof | FLUSHING OIL | Prioritas 2 | Operation | TU.401/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.069.22 | Valid | Valid |  | 11 Mei 2028 | Valid | 3060/PKTN.4.8/KHP/DL/10/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Non-functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-004/00 | Fixed roof | Slop Oil | Prioritas 2 | Operation | TU.393/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.070.22 | Valid | Valid |  | 15 Januari 2030 | Valid | 499/PKTN.4.8/KHP/DL/2/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Non-functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-005/00 | Fixed roof | Slop Oil | Prioritas 2 | Operation | TU.409/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.071.22 | Valid | Valid |  | 2024-04-20 | Valid | 527/PKTN.4.8/KHP/DL/06/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-006/00 | Fixed roof | Slop Oil | Prioritas 2 | Operation | TU.410/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.072.22 | Valid | Valid |  | 23 Mei 2032 | Valid | TU.2008/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-007/00 | Fixed roof | PTCF | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.073.22 | Valid | Valid |  | 14 Februari 2029 | Valid | 858/PKTN.4.8/KHP/DL/03/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Non-functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-008/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.074.22 | Valid | Valid |  | 03 Juli 2028 | Valid | 2389/PKTN.4.8/KHP/DL/08/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-009/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Overhaul/Cleaning | Idle | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.075.22 |  | Valid |  | 08 Oktober 2029 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-011/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 3 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.076.22 | Valid | Valid |  | 18 Maret 2029 | Valid | 1308/PKTN.4.8/KHP/DL/04/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA | NA |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-012/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 3 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.077.22 | Valid | Valid |  | 1930-09-12 | Valid | 2540/PKTN.4.8/KHP/DL/09/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-F-013/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 3 | Operation | TU.380/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.078.22 | Valid | Valid |  | 21 Februari 2024 | Valid | 233/PKTN.4.8/KHP/DL/03/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-G-001/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Operation | T.0650/PKTN.4.5/KN/09/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.079.22 | Valid | Valid |  | 05 Agustus 2029 | Valid | 2680/PKTN.4.8/KHP/DL/08/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-G-002/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Operation | TU.382/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.080.22 | Valid | Valid |  | 17 Juli 2033 | Valid | TU.2818/PKTN.4.5/KHP/DL/08/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-G-003/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.081.22 | Valid | Valid |  | 06 Agustus 2029 | Valid | 2681/PKTN.4.8/KHP/DL/08/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-G-004/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Operation | TU.373/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.082.22 | Valid | Valid |  | 01 Agustus 2029 | Valid | 872/PKTN.4.8/KHP/DL/8/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-G-005/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Operation | TU.370/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.083.22 | Valid | Valid |  | 31 Agustus 2028 | Valid | 946/PKTN.4.8/KHP/DL/09/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-H-001/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 2 | Operation | TU.388/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.084.22 | Valid | Valid |  | 25 Agustus 2032 | Valid | TU.3085/PKTN.4.8/KHP/DL/09/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-H-002/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 2 | Operation | TU.405/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.085.22 | Valid | Valid |  | 2024-04-23 | Valid | 528/PKTN.4.8/KHP/DL/06/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-H-003/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 2 | Overhaul/Cleaning | TU.374/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.086.22 |  | Valid |  | 04 Oktober 2029 | [78 empty] | Good | Good |  | Selesai 13-jan-25 | [48 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-H-004/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 3 | Operation | TU.385/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.087.22 | Valid | Valid |  | 15 Februari 2029 | Valid |  | good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-H-005/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 3 | Overhaul/Cleaning | Idle | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.088.22 |  | Valid |  | 23 Maret 2024 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-H-006/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 3 | Overhaul/Cleaning | Idle | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.089.22 |  | Valid |  | 2024-04-24 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-H-007/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 3 | Operation | TU.386/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | Fixed roof | Valid | Valid |  | 30 Januari 2031 | Valid | 144/PKTN.4.8/KHP/DL/02/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-H-008/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 3 | Operation | TU.392/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | Fixed roof | Valid | Valid |  | 15 Juli 2033 | Valid | TU.2816/PKTN.4.5/KHP/DL/08/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-K-001/00 | Fixed roof | SBPX 40B | Prioritas 3 | Operation | TU.362/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | Fixed roof | Valid | Valid |  | 1933-09-21 | Valid | TU.3335/PKTN.4.5/KHP/DL/10/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-K-002/00 | Fixed roof | SBPX 40B | Prioritas 3 | Operation | TU.360/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-04-07 | Fixed roof | Valid | Valid |  | 24 Januari 2031 | Valid | 146/PKTN.4.8/KHP/DL/02/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-K-003/00 | Fixed roof | Slop Oil | Prioritas 3 | Idle | TU.363/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 |  | 2026-04-07 | Fixed roof |  |  |  | 27 Januari 2031 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-K-004/00 | Fixed roof | SBPX 40B | Prioritas 3 | Operation | TU.407/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | Fixed roof | Valid | Overdue < 3 tahun |  | 28 Juni 2031 | Valid | 2612/PKTN.4.8/KHP/DL/07/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-K-005/00 | Fixed roof | SBPX 40B | Prioritas 3 | Operation | TU.414/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | Fixed roof | Valid | Valid |  | 14 Juli 2033 | Valid | TU.2815/PKTN.4.5/KHP/DL/08/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-K-009/00 | Fixed roof | Condensate Sei. Gerong | Prioritas 1 | Operation | TU.415/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 07 Juli 2023 | 029-03-PBC/1000035764/E08-L11/P8/2022 | Valid | Valid |  | 21 Januari 2030 | Valid | 497/PKTN.4.8/KHP/DL/2/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-K-010/00 | Fixed roof | Condensate Sei. Gerong | Prioritas 3 | Operation | TU.403/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 07 Juli 2023 | 029-04-PBC/1000035764/E08-L11/P8/2022 | Valid | Valid |  | 1933-09-26 | Valid | T.138/PKTN.4.5/KHP/DL/10/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-K-014/00 | Fixed roof | SBPX 40B | Prioritas 3 | Operation | TU.403/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | Fixed roof | Valid | Valid |  | 29 Agustus 2028 | Valid | 943/PKTN.4.8/KHP/DL/09/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-K-019/00 | Fixed roof | Condensate Sei. Gerong | Prioritas 3 | Operation | TU.403/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 23 Maret 2020 | 037/48-3/TP/IP/18.01/DJM.T/2016 | Valid | Valid |  | 17 Desember 2032 | Valid | T.635/PKTN.4.5/KHP/DL/12/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-K-020/00 | Fixed roof | Condensate Sei. Gerong | Prioritas 3 | Operation | TU.403/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.096.22 | Valid | Valid |  | 16 Mei 2029 | Valid | 641/PKTN.4.8/KHP/DL/05/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-L-001/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Operation | TU.384/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.097.22 | Valid | Valid |  | 23 Mei 2032 | Valid | TU.2005/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-L-002/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Overhaul/Cleaning | TU.377/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.098.22 | Valid | Valid |  | 1931-11-12 | Valid | 4118/PKTN.4.8/KHP/DL/11/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-L-003/00 | Fixed roof | LONG RESIDUE | Prioritas 2 | Operation | TU.413/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.099.22 | Valid | Valid |  | 30 Juni 2028 | Valid | 2385/PKTN.4.8/KHP/DL/08/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-L-004/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Operation | TU.371/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.100.22 | Valid | Valid |  | 27 Agustus 2032 | Valid | TU.3088/PKTN.4.8/KHP/DL/09/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-L-005/00 | Fixed roof | PTCF | Prioritas 2 | Operation | TU.375/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.101.22 | Valid | Valid |  | 1930-11-11 | Valid | 774/PKTN.4.8/KHP/DL/11/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-L-006/00 | Fixed roof | HVGO | Prioritas 2 | Operation | T.0081/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-04-07 | 029-08-PBC/1000035764/E08-L11/P8/2022 | Valid | Valid |  | 11 Oktober 2029 | Valid | 3624/PKTN.4.8/KHP/DL/10/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-001/00 | Fixed roof | Naphtha Intermedia | Prioritas 3 | Overhaul/Cleaning |  |  | Valid | 2026-09-20 | P009.NH.SA.102.22 | Valid | Valid |  | 30 Juni 2031 | Valid | 2608/PKTN.4.8/KHP/DL/07/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-002/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | TU.416/PKTN.4.5/SKHP/DL/02/2024 | 01 Maret 2026 | Valid | 2026-09-20 | P009.NH.SA.103.22 | Valid | Valid |  | 11 Agustus 2028 | Valid | 912/PKTN.4.8/KHP/DL/09/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-003/00 | Fixed roof | PERTALITE | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.104.22 | Valid | Valid |  | 18 Februari 2029 | Valid | 861/PKTN.4.8/KHP/DL/03/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-004/00 | Fixed roof | PERTAMAX | Prioritas 1 | Overhaul/Cleaning | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.105.22 | Valid | Valid |  | 14 Oktober 2029 | Valid | 3626/PKTN.4.8/KHP/DL/10/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-005/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2024-04-07 | 029-01-PBC/1000035764/E08-L11/P8/2022 | Valid | Valid |  | 17 Januari 2030 | Valid | 498/PKTN.4.8/KHP/DL/2/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-006/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Overhaul/Cleaning |  |  | Valid | 2026-09-20 | P009.NH.SA.106.22 | Valid | Valid |  | 20 Maret 2033 | Valid | TU.1232/PKTN.4.5/DL/04/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-008/00 | Fixed roof | PERTALITE | Prioritas 1 | Operation | Berita Acara Tera Ulang |  | Valid | 2026-09-20 | P009.NH.SA.107.22 | Valid | Valid |  | 30 Maret 2034 | Valid | T.77/PKTN.4.5/KHP/DL/04/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-009/00 | Fixed roof | PERTALITE | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.108.22 | Valid | Valid |  | 02 Juni 2028 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-010/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.109.22 | Valid | Overdue < 3 tahun |  | 06 Juli 2031 | Valid | 2607/PKTN.4.8/KHP/DL/07/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | 50% jumlah equipment foam chamber mengalami kerusakan / OSI tangki visual inspection not OK | Perbaikan Foam Chamber | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Not Good / Good With Note |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-011/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.110.22 | Valid | Valid |  | 23 Maret 2032 | Valid | T.266/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-013/00 | Fixed roof | PERTALITE | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.111.22 | Valid | Valid |  | 29 Agustus 2028 | Valid | 942/PKTN.4.8/KHP/DL/09/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-014/00 | Fixed roof | PERTALITE | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.112.22 | Valid | Valid |  | 29 Agustus 2032 | Valid |  | good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-015/00 | Fixed roof | HOMC | Prioritas 3 | Idle | TU.365/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 |  | 2026-09-20 | P009.NH.SA.113.22 |  |  |  | 27 Juni 2028 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-016/00 | Fixed roof | Naphtha Intermedia | Prioritas 3 | Overhaul/Cleaning | NA | 01 Januari 2030 |  | 2026-09-20 | P009.NH.SA.114.22 |  | Valid |  | 1930-09-06 | [10 empty] | NA | NA | [14 empty] | NA | NA | [14 empty] | NA | NA | [10 empty] | NA | NA | [42 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA | [6 empty] | NA | NA |  |  | NA | NA | [10 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-017/00 | Fixed roof | HOMC | Prioritas 3 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.115.22 | Valid | Valid |  | 30 Juni 2028 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-018/00 | Fixed roof | HOMC | Prioritas 3 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.116.22 | Valid | Valid |  |  | Valid | 1496/PKTN.4.8/KHP/DL/04/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-019/00 | Fixed roof | HOMC | Prioritas 3 | Operation | TU.404/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2022-09-27 | 5105-02-ENI/197/E08-L11/P1/2018 | Valid | Valid |  | 15 Desember 2032 | Valid | T.633/PKTN.4.5/KHP/DL/12/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-020/00 | Fixed roof | HOMC | Prioritas 1 | Operation | T.0082/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.118.22 | Valid | Valid |  | 1930-09-07 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-022/00 | Fixed roof | HOMC | Prioritas 3 | Operation | TU.396/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.120.22 | Valid | Valid |  | 08 Juli 2031 | Valid | 453/PKTN.4.8/KHP/DL/07/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-023/00 | Fixed roof | HOMC | Prioritas 3 | Overhaul/Cleaning | TU.366/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.121.22 |  | Valid |  | 1930-09-08 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-026/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | TU.432/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.122.22 | Valid | Valid |  | 09 Oktober 2029 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-O-027/00 | Fixed roof | Naphtha Intermedia | Prioritas 2 | Operation | TU.440/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.123.22 | Valid | Valid |  | 25 Maret 2032 | Valid | T.265/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-001/00 | Fixed roof | Crude Oil Arjuna | Prioritas 1 | Overhaul/Cleaning |  |  | Valid | 2026-09-20 | P009.NH.SA.124.22 | Valid | Valid |  | 12 Juli 2033 | Valid | TU.2813/PKTN.4.5/KHP/DL/08/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-002/00 | Fixed roof | Crude Oil Arjuna | Prioritas 1 | Operation | Ide | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.125.22 | Valid | Valid |  | 02 Juli 2028 | Valid | 2387/PKTN.4.8/KHP/DL/08/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-003/00 | Fixed roof | Crude Oil Minas | Prioritas 1 | Operation | TU.431/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.126.22 | Valid | Valid |  | 1933-09-23 | Valid | T.137/PKTN.4.5/KHP/DL/10/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-004/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.426/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.127.22 | Valid | Valid |  | 1930-11-09 | Valid | 772/PKTN.4.8/KHP/DL/11/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | 50% jumlah equipment foam chamber mengalami kerusakan / OSI tangki visual inspection not OK | Perbaikan Foam Chamber | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-005/00 | Fixed roof | Crude Oil Mixed 2 | Prioritas 1 | Operation | TU.424/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.128.22 | Valid | Valid |  | 16 Maret 2029 | Valid | 1307/PKTN.4.8/KHP/DL/04/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-006/00 | Fixed roof | Crude Oil Arjuna | Prioritas 1 | Operation | TU.435/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.129.22 | Valid | Valid |  | 22 Oktober 2032 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-007/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | T.0067/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.130.22 | Valid | Valid |  | 1933-09-28 | Valid | T.139/PKTN.4.5/KHP/DL/10/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Non-functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-008/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.131.22 | Valid | Valid |  | 30 Maret 2034 | Valid | T.75/PKTN.4.5/KHP/DL/04/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-009/00 | Fixed roof | CRUDE OIL | Prioritas 2 | Operation | TU.427/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.132.22 | Valid | Valid |  | 02 Februari 2031 | Valid | 468/PKTN.4.8/KHP/DL/02/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-010/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Overhaul/Cleaning | TU.394/PKTN.4.5/SKHP/DL/02/2024 | [5 empty] | Valid | [132 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-011/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Operation | TU.428/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.134.22 | Valid | Valid |  | 28 Maret 2032 | Valid | T.264/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Non-functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-012/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Operation | TU.406/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.135.22 | Valid | Valid |  | 19 Juli 2033 | Valid | T.111/PKTN.4.5/KHP/DL/08/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Non-functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-013/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Operation | TU.368/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.136.22 | Valid | Valid |  | 14 Mei 2028 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | 50% non-functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-014/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Overhaul/Cleaning | TU.429/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.137.22 |  | Valid |  | 30 Agustus 2028 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-015/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Operation | TU.401/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.138.22 | Valid | Valid |  | 06 Agustus 2029 | Valid | 873/PKTN.4.8/KHP/DL/08/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-016/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Operation | TU.400/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.139.22 | Valid | Valid |  | 1930-11-10 | Valid | 3500/PKTN.4.8/KHP/DL/11/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-017/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Operation | TU.423/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-04-07 | 029-02-PBC/1000035764/E08-L11/P8/2022 | Valid | Overdue < 3 tahun |  | 14 Maret 2029 | Valid | 1304/PKTN.4.8/KHP/DL/04/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-018/00 | Fixed roof | Crude Oil Arjuna | Prioritas 1 | Operation | TU.425/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.140.22 | Valid | Overdue > 3 tahun |  | 30 Juni 2031 | Valid | 2614/PKTN.4.8/KHP/DL/07/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-019/00 | Fixed roof | Crude Oil Mix 2 | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.141.22 | Valid | Valid |  | 30 Maret 2032 | Valid | T.263/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-020/00 | Fixed roof | Crude Oil Mix 2 | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.142.22 | Valid | Valid |  | 13 Maret 2029 | Valid | 1303/SPK.4.8/KHP/DL/04/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Non-functional | Kerusakan Pada Modul FCU |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-021/00 | Fixed roof | Crude Oil Mix 2 | Prioritas 2 | Operation | TU.430/PKTN.4.5/SKHP/DL/02/2023 | 24 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.143.22 | Valid | Overdue < 3 tahun |  | 20 Januari 2031 | Valid | 138/PKTN.4.8/KHP/DL/02/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-022/00 | Fixed roof | Crude Oil Mix 2 | Prioritas 1 | Operation | T.0459/PKTN.4.5/KN/02/2024 | 02 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.144.22 | Valid | Valid |  | 11 Februari 2034 | Valid | TU.681/PKTN.4.5/KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | 50% jumlah equipment foam chamber mengalami kerusakan / OSI tangki visual inspection not OK | Perbaikan Foam Chamber | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional | belum dilakukan penarikan kabel power & signal. | Pengaturan Pola Operasi dari Auto menjadi Manual | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-023/00 | Fixed roof | Crude Oil Mix 1 | Prioritas 1 | Operation | T.16/PKTN.4.5/SKHP/DL/02/2023 | 02 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.145.22 | Valid | Valid |  | 11 Juli 2033 | Valid | TU.2812/PKTN.4.5/KHP/DL/08/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-024/00 | Fixed roof | Crude Oil Mix 1 | Prioritas 1 | Operation | T.17/PKTN.4.5/SKHP/DL/02/2023 | 02 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.146.22 | Valid | Overdue > 3 tahun |  | 12 Juli 2033 | Valid | TU.2811/PKTN.4.5/KHP/DL/08/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-025/00 | Fixed roof | Crude Oil Mix 1 | Prioritas 1 | Overhaul/Cleaning | [6 empty] | Valid | [132 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-026/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.148.22 | Valid | Valid |  |  | Valid | 2539/PKTN.4.8/KHP/DL/09/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-027/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Operation | TU.403/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.149.22 | Valid | Valid |  | 27 Maret 2031 | Valid | 287/PKTN.4.8/KHP/DL/04/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-028/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Overhaul/Cleaning | [139 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-029/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Operation | TU.395/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.151.22 | Valid | Overdue < 3 tahun |  | 2024-04-23 | Valid | 529/PKTN.4.8/KHP/DL/06/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-030/00 | Fixed roof | Crude Oil Mix 3 | Prioritas 1 | Operation |  |  | Valid |  |  | Valid | Valid |  |  | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPPL | ITP-R-031/00 | Fixed roof | Crude Oil Banyu Urip | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.153.22 | Valid | Valid |  | 1931-11-17 | Valid | 918/PKTN.4.8/KHP/DL/11/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-011/00 | Fixed roof | SLOPS | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2025-11-07 | 029-16-PBC/1000035764/E08-L11/P8/2022 | Valid | Overdue > 3 tahun |  | 01 Januari 2030 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-012/00 | Fixed roof | SLOPS | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-21 | P009.NH.SA.154.22 | Valid | Overdue > 3 tahun |  | 01 Januari 2030 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-014/00 | Fixed roof | SLOPS | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.155.22 | Valid | Overdue < 3 tahun |  | 01 Januari 2030 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-015/00 | Fixed roof | SLOPS | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-21 | P009.NH.SA.156.22 | Valid | Overdue < 3 tahun |  | 01 Januari 2030 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-016/00 | Fixed roof | SLOPS | Prioritas 2 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.157.22 | Valid | Valid |  | 01 Januari 2030 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-017/00 | Fixed roof | SLOPS | Prioritas 2 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.158.22 | Valid | Valid |  | 01 Januari 2030 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-018/00 | Fixed roof | SLOPS | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.159.22 | Valid | Valid |  | 01 Januari 2030 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-019/00 | Fixed roof | SLOPS | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-21 | P009.NH.SA.160.22 | Valid | Valid |  | 01 Januari 2030 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-020/00 | Fixed roof | SLOPS | Prioritas 2 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.161.22 | Valid | Valid |  | 01 Januari 2030 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-025/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.162.22 | Valid | Valid |  | 17 Mei 2029 | Valid | 1798/PKTN.4.8/KHP/DL/05/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-026/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 2 | Overhaul/Cleaning | NA | 01 Januari 2030 |  | 2026-09-20 | P009.NH.SA.163.22 |  | Valid |  | 09 Maret 2028 | [10 empty] | NA | NA | [14 empty] | NA | NA | [14 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | [18 empty] | NA | NA | [6 empty] | NA | NA |  |  | NA | NA | [10 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | [10 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-030/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Idle | NA | 01 Januari 2030 |  | 2026-09-21 | P009.NH.SA.164.22 | [134 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-031/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Idle | NA | 01 Januari 2030 |  | 2026-09-21 | P009.NH.SA.165.22 |  |  |  | 20 Januari 2030 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-032/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Idle | NA | 01 Januari 2030 |  | 2026-09-21 | P009.NH.SA.166.22 |  |  |  | 08 Maret 2024 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-033/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Idle | NA | 01 Januari 2030 |  | 2026-09-21 | P009.NH.SA.167.22 |  |  |  | 08 Agustus 2028 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-044/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.402/PKTN.4.5/SKHP/DL/02/2024 | 15 Januari 2026 | Valid | 2026-04-07 | Fixed roof | Valid | Valid |  | 26 Januari 2031 | Valid | 145/PKTN.4.8/KHP/DL/02/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-045/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | T.0068/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.168.22 | Valid | Valid |  | 31 Agustus 2032 | Valid | T.520/PKTN.4.8/KHP/DL/09/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-046/00 | Fixed roof | SLOPS | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.169.22 | Valid | Valid |  | 01 Januari 2030 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-075/00 | Fixed roof | Slop Oil | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2022-09-27 | 5159-02-ENI/197/E08-L11/P1/2018 | Valid | Valid |  | 17 Desember 2032 | Valid | T.632/PKTN.4.5/KHP/DL/12/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-076/00 | Fixed roof | FLUSHING OIL | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.171.22 | Valid | Valid |  | 03 Mei 2034 | Valid | TU.1523/PKTN.4.8/KHP/DL/05/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  | Selesai 16-Jan-25 | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | 50% non-functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-077/00 | Fixed roof | DECANT OIL | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.172.22 | Valid | Valid |  |  | Valid | 198/PKTN.4.8/KHP/DL/01/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-078/00 | Fixed roof | DECANT OIL | Prioritas 2 | Operation |  |  | Valid | 2026-09-20 | P009.NH.SA.173.22 | Valid | Valid |  |  | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-079/00 | Fixed roof | DECANT OIL | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.174.22 | Valid | Valid |  | 17 Mei 2029 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-080/00 | Fixed roof | Slop Oil | Prioritas 2 | Operation | T.0069/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.175.22 | Valid | Valid |  | 16 Februari 2024 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-081/00 | Fixed roof | FLUSHING OIL | Prioritas 2 | Operation | TU.408/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.176.22 | Valid | Valid |  | 18 Juli 2033 | Valid | TU.2819/PKTN.4.5/PKTN/DL/08/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-082/00 | Fixed roof | DECANT OIL | Prioritas 2 | Operation | T.0070/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2022-09-27 | 5166-02-ENI/197/E08-L11/P1/2018 | Valid | Valid |  | 19 Desember 2032 | Valid | T.637/PKTN.4.5/KHP/DL/12/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-083/00 | Fixed roof | LSFO | Prioritas 3 | Operation | T.0083/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.178.22 | Valid | Valid |  | 14 Maret 2032 | Valid | T.269/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-084/00 | Fixed roof | LSFO | Prioritas 3 | Operation | TU.407/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.179.22 | Valid | Valid |  | 1930-11-12 | Valid | 775/PKTN.4.8/KHP/DL/11/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-085/00 | Fixed roof | LSFO | Prioritas 3 | Operation | NA | 01 Januari 2030 | Valid | 2022-09-27 | 5169-02-ENI/197/E08-L11/P1/2018 | Valid | Valid |  | 20 Maret 2033 | Valid | T.57/PKTN.4.5/DL/04/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-090/00 | Fixed roof | DECANT OIL | Prioritas 2 | Overhaul/Cleaning | TU.414/PKTN.4.5/SKHP/DL/02/2024 | [5 empty] | Valid | [132 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-091/00 | Fixed roof | LSFO | Prioritas 2 | Operation | T.0088/PKTN.4.5/KN/01/2023 | 16 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.182.22 | Valid | Valid |  | 29 Maret 2034 | Valid | TU.1445/PKTN.4.5/KHP/DL/04/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  | Selesai 14-jan-25 | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-092/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 2 | Operation | T.0097/PKTN.4.5/KN/01/2023 | 16 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.183.22 | Valid | Valid |  | 28 Mei 2032 | Valid | T.448/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-150/00 | Fixed roof | Slop Oil | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.184.22 | Valid | Overdue > 3 tahun |  | 28 Januari 2031 | Valid | 467/PKTN.4.8/KHP/DL/02/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-151/00 | Fixed roof | Crude Oil Banyu Urip | Prioritas 2 | Operation | TU.411/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-04-07 | 029-14-PBC/1000035764/E08-L11/P8/2022 | Valid | Valid |  | 1931-04-02 | Valid | 288/PKTN.4.8/KHP/DL/04/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Not Good | Non-functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-152/00 | Fixed roof | Slop Oil | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.185.22 | Valid | Overdue > 3 tahun |  | 05 Juli 2031 | Valid | 2615/PKTN.4.8/KHP/DL/07/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-153/00 | Fixed roof | Slop Oil | Prioritas 2 | Overhaul/Cleaning | T.0071/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.186.22 |  | Valid |  | 08 Februari 2034 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-154/00 | Fixed roof | Slop Oil | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2025-11-07 | 029-13-PBC/1000035764/E08-L11/P8/2022 | Valid | Overdue < 3 tahun |  | 2028-04-07 | Valid | 769/PKTN.4.8./KHP/DL/08/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-158/00 | Fixed roof | Naphtha Intermedia | Prioritas 2 | Operation | T.0084/PKTN.4.8/KN/07/2022 |  | Valid | 2026-09-20 | P009.NH.SA.187.22 | Valid | Valid |  |  | Valid | 919/PKTN.4.8/KHP/DL/11/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-159/00 | Fixed roof | Naphtha Intermedia | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.188.22 | Valid | Valid |  | 18 Februari 2031 | Valid | T.18/PKTN.4.5/SKHP/DL/02/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-160/00 | Fixed roof | Naphtha Intermedia | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.189.22 | Valid | Valid |  | 02 Februari 2031 | Valid | 461/PKTN.4.8/KHP/DL/02/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-191/00 | Fixed roof | POD | Prioritas 3 | Operation | TU.410/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.190.22 | Valid | Valid |  | 27 Maret 2034 | Valid | TU.1444/PKTN.4.5/KHP/DL/04/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional | 50% tidak berfungsi | Perbaikan Tank Heater | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-192/00 | Fixed roof | POD | Prioritas 3 | Operation | T.0072/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2022-09-27 | 5180-02-ENI/197/E08-L11/P1/2018 | Valid | Valid |  | 30 Januari 2033 | Valid | T.09/PKTN.4.5/DL/02/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-200/00 | Fixed roof | LONG RESIDUE | Prioritas 2 | Overhaul/Cleaning |  |  | Valid | 2026-09-20 | P009.NH.SA.191.22 | Valid | Valid |  |  | Valid | 4131/PKTN.4.8/KHP/DL/11/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-201/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Operation | T.26/PKTN.4.5/SKHP/DL/02/2023 | 01 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.193.22 | Valid | Valid |  | 16 Mei 2029 | Valid | 1805/PKTN.4.8/KHP/DL/05/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-202/00 | Fixed roof | LONG RESIDUE | Prioritas 3 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.194.22 | Valid | Valid |  | 2029-09-27 | Valid |  | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-203/00 | Fixed roof | LSFO | Prioritas 3 | Overhaul/Cleaning |  |  | Valid | 2026-09-20 | P009.NH.SA.195.22 | Valid | Valid |  | 12 Maret 2032 | Valid | TU.1214/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-204/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Overhaul/Cleaning | TU.409/PKTN.4.5/SKHP/DL/02/2024 | 16 Januari 2026 | Valid | 2026-09-20 | P009.NH.SA.196.22 |  | Valid |  | 2029-09-27 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-205/00 | Fixed roof | CRUDE OIL | Prioritas 3 | Operation | T.0085/PKTN.4.8/KN/07/2022 | 14 Juli 2024 | Valid | 2026-09-20 | P009.NH.SA.197.22 | Valid | Overdue < 3 tahun |  | 30 Mei 2032 | Valid | T.447/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-206/00 | Fixed roof | MFO Low Sulphur 180 CST | Prioritas 2 | Operation | TU.417/PKTN.4.5/SKHP/DL/02/2024 | 31 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.198.22 | Valid | Valid |  | 1933-09-29 | Valid | T.140/PKTN.4.5/KHP/DL/10/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-207/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 23 Maret 2020 | 046/48-3/TP/IP/18.01/DJM.T/2016 | Valid | Valid |  | 30 Januari 2033 | Valid | T.12/PKTN.4.5/DL/02/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-208/00 | Fixed roof | Crude Oil Banyu Urip | Prioritas 1 | Operation | TU.489/PKTN.4.5/SKHP/DL/02/2023 | 31 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.199.22 | Valid | Valid |  | 15 Oktober 2029 | Valid | 1227/PKTN.4.8/KHP/DL/10/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-209/00 | Fixed roof | LSFO | Prioritas 2 | Operation | T.58/PKTN.4.5/SKHP/DL/04/2023 | 2024-04-11 | Valid | 2026-09-20 | P009.NH.SA.200.22 | Valid | Valid |  | 08 Februari 2029 | Valid | 260/PKTN.4.8/S/DL/02/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional | Non-functional/ Hydrocarbon release/ Handwheel Hilang | Perbaikan Gate Valve. Selesaii 15-Jan-25 | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-210/00 | Fixed roof | LSFO | Prioritas 2 | Operation | TU.486/PKTN.4.5/SKHP/DL/02/2023 | 01 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.201.22 | Valid | Valid |  | 1930-11-13 | Valid | 783/PKTN.4.8/KHP/DL/11/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA | NA | NA | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-211/00 | Fixed roof | LSFO | Prioritas 2 | Operation | T.27/PKTN.4.5/SKHP/DL/02/2023 | 01 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.202.22 | Valid | Valid |  | 04 Juli 2029 | Valid |  | good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-212/00 | Fixed roof | FLUSHING OIL | Prioritas 2 | Operation | T.59/PKTN.4.5/SKHP/DL/04/2023 |  | Valid | 2026-09-20 | P009.NH.SA.203.22 | Valid | Valid |  |  | Valid | 1031/PKTN.4.8/KHP/DL/04/2018 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-213/00 | Fixed roof | FLUSHING OIL | Prioritas 2 | Operation | TU.364/PTKN.4.5/SKHP/DL/02/2024 |  | Valid | 2026-09-20 | P009.NH.SA.204.22 | Valid | Valid |  |  | Valid | TU.441/PKTN.4.5/SKHP/DL/02/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-214/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Overhaul/Cleaning | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.205.22 |  | Valid |  | 30 Maret 2031 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-215/00 | Fixed roof | FLUSHING OIL | Prioritas 2 | Operation | TU.381/PKTN.4.5/SKHP/DL/02/2024 |  | Valid | 2026-09-20 | P009.NH.SA.206.22 | Valid | Valid |  |  | Valid | TU.442/PKTN.4.5/SKHP/DL/02/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-216/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | T.19/PKTN.4.5/SKHP/DL/02/2023 | 02 Februari 2025 | Valid | 2022-09-27 | 5196-02-ENI/197/E08-L11/P1/2018 | Valid | Valid |  | 24 Oktober 2032 | Valid | T.616/PKTN.4.8?KHP/DL/11/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-217/00 | Fixed roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | T.0460/PKTN.4.5/KN/02/2024 | 13 Februari 2026 | Valid | 2026-09-20 | Fixed roof | Valid | Valid |  | 17 Januari 2029 | Valid | 166/PKTN.4.8/S/DL/02/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | Terdapat hidrocarbon release | Perbaikan gauge hatch. Selesai 16-Jan-25 | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-218/00 | Fixed roof | BIO FAME | Prioritas 2 | Operation | TU.480/PKTN.4.5/SKHP/DL/02/2023 | 02 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.209.22 | Valid | Valid |  | 05 Mei 2034 | Valid | TU.1524/PKTN.4.8/KHP/DL/05/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-219/00 | Fixed roof | BIO FAME | Prioritas 2 | Operation | T.18/PKTN.4.5/SKHP/DL/02/2023 | 02 Februari 2025 | Valid | 2026-09-20 | Fixed roof | Valid | Valid |  | 20 Maret 2030 | Valid | 259/PKTN.4.8/KHP/DL/6/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-221/00 | Fixed roof | HOMC | Prioritas 1 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.211.22 | Valid | Valid |  | 1933-11-28 | Valid | [9 empty] | NA | NA | [14 empty] | NA | NA | [14 empty] | NA | NA | [10 empty] | NA | NA | [14 empty] | NA | NA |  |  | NA | NA | [10 empty] | NA | NA | [10 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | [6 empty] | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-222/00 | Fixed roof | HOMC | Prioritas 1 | Operation | Berita Acara Tera Ulang | 24 Februari 2026 | Valid | 2026-09-20 | P009.NH.SA.212.22 | Valid | Valid |  | 2029-09-27 | Valid | 1229/PKTN.4.8/KHP/DL/10/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-223/00 | Fixed roof | FLUSHING OIL | Prioritas 2 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.213.22 | Valid | Valid |  | 02 Februari 2034 | Valid | T.23/PKTN.4.5/KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-224/00 | Floating roof | HOMC | Prioritas 1 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.214.22 |  | Valid |  | 1933-11-22 | [6 empty] | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA | NA | NA | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-225/00 | Floating roof | HOMC | Prioritas 1 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.215.22 | Valid | Valid |  | 29 Agustus 2032 | Valid | T.519/PKTN.4.8/KHP/DL/09/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-226/00 | Fixed roof | HOMC | Prioritas 3 | Operation | TU.415/PKTN.4.5/SKHP/DL/02/2024 | 08 Januari 2025 | Valid | 2026-09-20 | P009.NH.SA.216.22 | Valid | Valid |  | 21 Maret 2030 | Valid | 516 /PKTN.4.8/KHP/DL/9/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-227/00 | Floating roof | HOMC | Prioritas 1 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.217.22 |  | Valid |  | 07 Mei 2034 | [130 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-230/00 | Floating roof | HOMC | Prioritas 1 | Idle | NA | 01 Januari 2030 |  | 2026-09-20 | P009.NH.SA.218.22 |  |  |  | 15 Oktober 2029 | [10 empty] | NA | NA | [14 empty] | NA | NA | [14 empty] | NA | NA | [10 empty] | NA | NA | [42 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA | [6 empty] | NA | NA |  |  | NA | NA | [10 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-231/00 | Floating roof | HOMC | Prioritas 1 | Idle | NA | 01 Januari 2030 |  | 2026-09-20 | P009.NH.SA.219.22 |  |  |  | 14 Februari 2029 | [10 empty] | NA | NA | [14 empty] | NA | NA | [14 empty] | NA | NA | [10 empty] | NA | NA | [42 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA | [6 empty] | NA | NA |  |  | NA | NA | [10 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-247/00 | Floating roof | Naphtha Intermedia | Prioritas 1 | Overhaul/Cleaning | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.220.22 | Valid | Valid |  |  | Valid | [9 empty] | NA | NA | [14 empty] | NA | NA | [14 empty] | NA | NA | [10 empty] | NA | NA | [14 empty] | NA | NA |  |  | NA | NA | [10 empty] | NA | NA | [10 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | [6 empty] | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-249/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation |  |  | Valid |  |  | Valid | Valid |  |  | Valid |  | good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-250/00 | Floating roof | Naphtha Intermedia | Prioritas 1 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.222.22 | Valid | Valid |  | 22 Oktober 2032 | Valid | TU.3841/PKTN.4.8/KHP/DL/11/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA | NA | NA | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-251/00 | Floating roof | Naphtha Intermedia | Prioritas 1 | Operation | NA | 01 Januari 2030 | Valid | 2026-09-20 | P009.NH.SA.223.22 | Valid | Valid |  | 17 Maret 2033 | Valid | TU.1230/PKTN.4.8/KHP/DL/01/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA | NA | NA | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-253/00 | Fixed roof | Crude Oil Grissik Mix Condensate | Prioritas 1 | Operation | TU.485/PKTN.4.5/SKHP/DL/02/2023 | 01 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.224.22 | Valid | Valid |  | 24 Mei 2032 | Valid | TU.2006/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-254/00 | Fixed roof | Crude Oil | Prioritas 1 | Operation | T.0458/PKTN.4.5/KN/02/2024 | 01 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.225.22 | Valid | Valid |  | 1930-09-04 | Valid | 2532/PKTN.4.8/KHP/DL/09/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-256/00 | Fixed roof | Crude Oil | Prioritas 1 | Overhaul/Cleaning | [6 empty] | Valid | [132 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-257/00 | Fixed roof | Crude Oil Arjuna | Prioritas 1 | Operation | T.22/PKTN.4.5/SKHP/DL/02/2023 | 02 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.227.22 | Valid | Valid |  | 29 Maret 2034 | Valid | TU.1443/PKTN.4.5/KHP/DL/04/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  | Perbaikan. Selesai 15-Jan-2025 | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-258/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Overhaul/Cleaning | T.23/PKTN.4.5/SKHP/DL/02/2023 | 02 Februari 2025 |  | 2026-09-20 | P009.NH.SA.228.22 |  | Valid |  | 25 Mei 2032 | [10 empty] | NA | NA | [14 empty] | NA | NA | [14 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | [14 empty] | Good | Functional | [14 empty] | NA | NA | [10 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | [10 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-259/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Overhaul/Cleaning | TU.487/PKTN.4.5/SKHP/DL/02/2023 | 31 Januari 2025 |  | 2026-09-20 | P009.NH.SA.223.22 |  | Valid |  | 13 Februari 2029 | [10 empty] | NA | NA | [14 empty] | NA | NA | [14 empty] | NA | NA |  |  | Good | Functional | [6 empty] | NA | NA | [14 empty] | NA | NA |  |  | NA | NA | [10 empty] | NA | NA | [10 empty] | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | [10 empty] | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-260/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | T.28/PKTN.4.5/SKHP/DL/02/2023 | 31 Januari 2025 | Valid | 2022-09-27 | 5219-02-ENI/197/E08-L11/P1/2018 | Valid | Valid |  | 27 Januari 2031 | Valid | T.10/PKTN/4.5/DL/02/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-261/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | TU.367/PKTN.4.5/SKHP/DL/02/2024 | 10 Januari 2026 | Valid | 2026-09-20 | P009.NH.SA.231.22 | Valid | Valid |  | 16 Maret 2032 | Valid | T.270/PKTN.4.8/KHP/DL/4/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-262/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | TU.484/PKTN.4.5/SKHP/DL/02/2023 | 01 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.232.22 | Valid | Valid |  | 17 Februari 2024 | Valid |  | good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-263/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | T.0461/PKTN.4.5/KN/02/2024 | 02 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.233.22 | Valid | Valid |  | 08 Mei 2034 | Valid | TU.1526/PKTN.4.8/KHP/DL/05/2024 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | Foam Chamber mengalami kerusakan | Perbaikan Foam Chamber | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Over 40% corrosion on primer layer | Cat Terkorosi >40% di primer layer | Monthly Onstream Inspection dan Plant Patrol | Good | Functional |  |  | 2026-07-28
RU III Plaju | RU03-PROD1-ITP | RU03-PROD1-ITP -ITPSG | ITP-T-264/00 | Fixed roof | Naphtha Intermedia | Prioritas 1 | Operation | TU.483/PKTN.4.5/SKHP/DL/02/2023 | 01 Februari 2025 | Valid | 2026-09-20 | P009.NH.SA.234.22 | Valid | Valid |  | 16 Januari 2029 | Valid | 165/PKTN.4.8/S/DL/02/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-FOC2 | RU04-FOC2 -U016 | 016T101/00 | Fixed Roof | CAUSTIC | Prioritas 2 | Idle | NA | NA | NA | NA | NA | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-FOC2 | RU04-FOC2 -U017 | 017T101/00 | Fixed Roof | CAUSTIC | Prioritas 2 | Idle | NA | NA | NA | NA | NA | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T112/00 | Fixed Roof | LMO RAFF | Prioritas 3 | Operation | TU.5269/PKTN.4.5/DL/09/2024 | 2026-10-12 | Valid | 2027-05-31 | 0127/SQ/ST/X/2023 | Valid | Valid |  | NA | Valid | TU. 2450/PKTN.4.5/KHP/DL/06/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U31 | 31T7/00 | Floating Roof | PERTAMAX | Prioritas 1 | Overhaul/Cleaning | TU.1325/PKTN.4.5/SKHP/DL/04/2024 | 2024-04-01 | Expired | 2027-05-31 | 0074/SQ/ST/XII/2023 | Valid | Valid |  | 2030-03-20 | Valid | 1112/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T116/00 | Fixed Roof | LMO DIST | Prioritas 3 | Operation | TU.3665/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2027-05-31 | 0131/SQ/ST/XII/2023 | Valid | Valid |  | NA | Valid | 3983/PKTN.4.8/KHP/DL/12/2018 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T117/00 | Fixed Roof | MMO DIST | Prioritas 3 | Operation | TU.3664/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2027-05-31 | 0132/SQ/ST/XII/2023 | Valid | Valid |  | NA | Valid | TU.3666/PKTN.4.5/KHP/DL/11/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T118/00 | Fixed Roof | DAO DIST | Prioritas 3 | Overhaul/Cleaning | TU.3666/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2027-05-31 | 0133/SQ/ST/XII/2023 | Valid | Valid |  | NA | Valid | TU.3665/PKTN.4.5/KHP/DL/11/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T119/00 | Fixed Roof | MINAREX-BHYB | Prioritas 3 | Operation | TU.3735/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2027-05-31 | 0134/SQ/ST/XII/2023 | Valid | Valid |  | 2028-11-21 | Valid | 3988/PKTN.4.8/KHP/DL/12/2018 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U38 | 38T106/00 | Floating Roof | MIX CRUDE | Prioritas 1 | Overhaul/Cleaning | 1795/PKTN.4.8/SKHP/DL/05/2022 | 2024-08-31 | Expired | 2027-05-21 | E00809/AOBJAR | Valid | Valid |  | 2032-04-24 | Valid | TU.1670/PKTN.4.8/KHP/DL/05/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | Thinning korosi pada roof | Dilakukan wrapping dan repainting roof | Good | Functional |  |  | Good | Functional | tidak pernah di operasikan |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T121/00 | Fixed Roof | SHORT RESIDUE | Prioritas 3 | Operation | TU.6760/PKTN.4.5/DL/08/2025 | 2027-07-25 | Valid | 2027-05-31 | 0112/SQ/ST/X/2023 | Valid | Valid |  | NA | Valid | TU.6585/PKTN.4.5/DL/07/2025 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T122/00 | Fixed Roof | REF FUEL OIL | Prioritas 2 | Operation | TU.3736/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2027-05-31 | 0136/SQ/ST/X/2023 | Valid | Valid |  | 2028-11-30 | Valid | 3989/PKTN.4.8/KHP/DL/12/2018 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T301/00 | Fixed Roof | LMO DIST | Prioritas 3 | Operation | TU.3737/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2026-12-19 | P005.NH.EW.006.23 | Valid | Valid |  | NA | Valid | 1928/PKTN.4.8/KHP/DL/05/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T302/00 | Fixed Roof | MMO DIST | Prioritas 3 | Overhaul/Cleaning | TU.3738/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2026-12-19 | P005.NH.EW.007.23 | Valid | Valid |  | NA | Valid | 1925/PKTN.4.8/KHP/DL/05/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T303/00 | Fixed Roof | DAO DIST | Prioritas 3 | Operation | TU.3667/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2026-12-19 | P005.NH.EW.008.23 | Valid | Valid |  | NA | Valid | 1925/PKTN.4.8/KHP/DL/05/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Korosi dan deformasi menyebabkan air menggenang (kedalaman ±10cm) disekitar rolling ladder | Telah dilakukan perbaikan temporer dengan metode FRP | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T304/00 | Fixed Roof | LMO HDT | Prioritas 3 | Operation | TU.0361/PKTN.4.5/DL/01/2025 | 2027-01-12 | Valid | 2026-12-19 | P005.NH.EW.009.23 | Valid | Valid |  | NA | Valid | TU.3310/PKTN.4.5/KHP/DL/09/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T305/00 | Fixed Roof | LMO HDT | Prioritas 3 | Overhaul/Cleaning | TU.3669/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2026-12-19 | P005.NH.EW.010.23 | Valid | Valid |  | NA | Valid | TU.3304/PKTN.4.5/KHP/DL/09/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T306/00 | Fixed Roof | MMO HDT | Prioritas 3 | Operation | TU.3671/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2026-12-19 | P005.NH.EW.011.23 | Valid | Valid |  | NA | Valid | TU.3303/PKTN.4.5/KHP/DL/09/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T307/00 | Fixed Roof | MMO HDT | Prioritas 3 | Operation | TU.3739/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2026-12-19 | P005.NH.EW.012.23 | Valid | Valid |  | NA | Valid | TU.3307/PKTN.4.5/KHP/DL/09/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T308/00 | Fixed Roof | DAO HDT RAFF | Prioritas 3 | Operation | TU.3670/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2026-12-19 | P005.NH.EW.013.23 | Valid | Valid |  | NA | Valid | 1481/PKTN.4.8/KHP/DL/05/2019 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T309/00 | Fixed Roof | DAO HDT RAFF | Prioritas 3 | Operation | TU.3740/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2026-12-19 | P005.NH.EW.014.23 | Valid | Valid |  | NA | Valid | TU.3308/PKTN.4.5/KHP/DL/09/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T310/00 | Fixed Roof | SHORT RESIDUE | Prioritas 3 | Operation | TU.6761/PKTN.4.5/DL/08/2025 | 2027-07-25 | Valid | 2026-12-19 | P005.NH.EW.015.23 | Valid | Valid |  | 2026-09-20 | Valid | Berita Acara (20/09/2024) | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T311/00 | Fixed Roof | SHORT RESIDUE | Prioritas 3 | Operation | TU.3663/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2026-12-19 | P005.NH.EW.059.23 | Valid | Valid |  | 2027-06-13 | Valid | TU.9583/PKTN.4.5/DL/09/2025 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T314/00 | Fixed Roof | ASPHALT-60/70 | Prioritas 3 | Operation | BA Tera Ulang | 2028-03-15 | Valid | 2026-12-19 | P005.NH.EW.061.23 | Valid | Valid |  | 2025-12-29 | Valid | BA Tera Ulang | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T315/00 | Fixed Roof | MMO RAFF | Prioritas 3 | Operation | TU.3657/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2026-12-19 | P005.NH.EW.016.23 | Valid | Valid |  | 2031-01-31 | Valid | 2287/PKTN.4.8/KHP/DL/06/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T316/00 | Fixed Roof | DAO RAFF | Prioritas 3 | Operation | TU.3662/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2026-12-19 | P005.NH.EW.017.23 | Valid | Valid |  | 2031-11-30 | Valid | 1355/PKTN.4.8/KHP/DL/05/2019 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T317/00 | Fixed Roof | MDU SLOPS | Prioritas 2 | Operation | TU.3741/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2026-12-19 | P005.NH.EW.019.23 | Valid | Valid |  | NA | Valid | 1931/PKTN.4.8/KHP/DL/05/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-UTL | RU04-UTL -U057 | 057T101/00 | Fixed Roof | Fuel Oil Tank | Prioritas 2 | Operation | NA | NA | NA | 2027-11-20 | 0169/SQ/ST/XII/2023 | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-FOC1 | RU04-FOC1 -U16 | 16T1/00 | Fixed Roof | CAUSTIC | Prioritas 2 | Operation | NA | NA | NA | 2027-11-20 | 0218/SQ/ST/XII/2023 | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-FOC1 | RU04-FOC1 -U16 | 16T2/00 | Fixed Roof | CAUSTIC | Prioritas 2 | Operation | NA | NA | NA | 2027-11-20 | 0219/SQ/ST/XII/2023 | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-FOC1 | RU04-FOC1 -U16 | 16T3/00 | Fixed Roof | CAUSTIC | Prioritas 2 | Operation | NA | NA | NA | 2027-11-20 | 0220/SQ/ST/XII/2023 | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U31 | 31T1/00 | Floating Roof | MIXED NAPHTHA | Prioritas 1 | Overhaul/Cleaning | TU.1323/PKTN.4.5/SKHP/DL/04/2024 | 2024-04-01 | Expired | 2027-11-20 | 056/SQ/SAU/XII/2023 | Valid | Valid |  | 2030-03-16 | Valid | 1969/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U31 | 31T2/00 | Floating Roof | PERTAMAX | Prioritas 1 | Operation | TU.1324/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2027-05-31 | 0069/SQ/ST/XII/2023 | Valid | Valid |  | 2031-11-05 | Valid | 1125/PKTN.4.8/KHP/DL/12/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U31 | 31T3/00 | Floating Roof | PERTAMAX | Prioritas 1 | Operation | TU.5674/PKTN.4.5/DL/11/2024 | 2026-09-28 | Valid | 2027-05-31 | 0070/SQ/ST/XII/2023 | Valid | Valid |  | 2032-03-31 | Valid | T.275/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U31 | 31T4/00 | Fixed Roof | NAPHTHA | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0071/SQ/ST/XII/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T5/00 | Fixed Roof | HVI-60 | Prioritas 3 | Operation | TU.28.33/PKTN.4.5/DL/04/2025 | 2027-03-21 | Valid | 2027-11-20 | 077/SQ/SAU/XII/2023 | Valid | Valid |  | 2033-05-31 | Valid | TU.1802/PKTN.4.5/KHP.DL/06/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U34 | 34T101/00 | Fixed Roof | IDO / HVGO | Prioritas 2 | Operation | TU.1328/PKTN.4.5/SKHP/DL/04/2024 | 2024-04-01 | Expired | 2027-11-20 | 090/SQ/SAU/XII/2023 | Valid | Valid |  | 2028-11-14 | Valid | 1352/PKTN.4.8/KHP/DL/05/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Korosi dan deformasi menyebabkan air menggenang (kedalaman ±10cm) disekitar rolling ladder | Telah dilakukan perbaikan temporer dengan metode FRP | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T114/00 | Fixed Roof | DAO RAFF | Prioritas 3 | Operation | TU.3734/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2027-05-31 | 0129/SQ/ST/X/2023 | Valid | Overdue < 3 Tahun |  | NA | Valid | TU.3312/PKTN.4.5/KHP/DL/09/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T120/00 | Fixed Roof | MDU SLOPS | Prioritas 2 | Operation | TU.3724/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2027-05-31 | 0135/SQ/ST/X/2023 | Valid | Overdue > 3 tahun |  | NA | Valid | TU. 2452/PKTN.4.5/KHP/DL/06/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U31 | 31T5/00 | Floating Roof | MOGAS COMP | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0072/SQ/ST/XII/2023 | Valid | Overdue < 3 Tahun |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U31 | 31T6/00 | Fixed Roof | NAPHTHA | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0073/SQ/ST/XII/2023 | Valid | Overdue < 3 Tahun |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U32 | 32T103/00 | Fixed Roof | SOLAR | Prioritas 2 | Operation | TU.7390/PKTN.4.5/DL/08/2025 | 2027-08-08 | Valid | 2027-05-31 | 0118/SQ/ST/XII/2023 | Valid | Valid |  | 2031-09-20 | Valid | R.T.10732/PKTN.4.5/DL/10/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U32 | 32T1/00 | Fixed Roof | Kerosine | Prioritas 2 | Overhaul/Cleaning | TU.6555/PKTN.4.5/SKHP/DL/07/2025 | 2027-07-18 | Valid | 2027-11-20 | 057/SQ/SAU/XII/2023 | Valid | Overdue > 3 tahun |  | 2031-05-31 | Valid | 1962/PKTN.4.8/KHP/DL/05/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U32 | 32T101/00 | Fixed Roof | AVTUR | Prioritas 2 | Operation | TU.3706/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2027-05-31 | 0116/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | 2031-05-21 | Valid | 2283/PKTN.4.8/KHP/DL/06/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U32 | 32T102/00 | Fixed Roof | Kerosine | Prioritas 2 | Operation | TU.1374/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-27 | Valid | 2027-05-31 | 0117/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | 2031-05-22 | Valid | 2284/PKTN.4.8/KHP/DL/06/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U32 | 32T104/00 | Fixed Roof | PERTAMAX | Prioritas 1 | Operation | TU.5464/PKTN.4.5/DL/07/2025 | 2027-06-20 | Valid | 2027-11-20 | 0236/SQ/ST/XII/2023 | Valid | Overdue < 3 Tahun |  | 2031-05-21 | Valid | 2803/PKTN.4.8/KHP/DL/06/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | terdapat 2 FGDS, 1 rusak | proses pengadaan material sensor FGDS | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U32 | 32T105/00 | Floating Roof | PERTALITE | Prioritas 1 | Operation | TU.1375/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-28 | Valid | 2027-05-31 | 0111/SQ/ST/X/2023 | Valid | Overdue < 3 Tahun |  | 2031-05-31 | Valid | 2285/PKTN.4.8/KHP/DL/06/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U32 | 32T2/00 | Fixed Roof | AVTUR | Prioritas 2 | Operation | TU.3563/PKTN.4.5/DL/05/2025 | 2027-03-21 | Valid | 2027-11-20 | 058/SQ/SAU/XII/2023 | Valid | Overdue > 3 tahun |  | 2031-05-31 | Valid | 1963/PKTN.4.8/KHP/DL/05/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U33 | 33T101/00 | Fixed Roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | TU.5458/PKTN.4.5/DL/07/2025 | 2027-06-20 | Valid | 2027-11-20 | 088/SQ/ST/XII/2023 | Valid | Valid |  | 2030-03-16 | Valid | 1116/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U33 | 33T102/00 | Fixed Roof | Solar/HSD/MGO/ADO | Prioritas 2 | Overhaul/Cleaning | TU.6556/PKTN.4.5/SKHP/DL/07/2025 | 2027-07-18 | Valid | 2027-11-20 | 089/SQ/ST/XII/2023 | Valid | Valid |  | 2030-03-16 | Valid | 1117/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U32 | 32T3/00 | Fixed Roof | AVTUR | Prioritas 2 | Operation | TU.2834/PKTN.4.5/DL/04/2025 | 2027-03-21 | Valid | 2027-11-20 | 059/SQ/SAU/XII/2023 | Valid | Overdue < 3 Tahun |  | 2030-03-20 | Valid | 1109/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U33 | 33T3/00 | Fixed Roof | MFO | Prioritas 2 | Operation | TU.5467/PKTN.4.5/DL/07/2025 | 2027-06-20 | Valid | 2027-11-20 | 061/SQ/SAU/XII/2023 | Valid | Valid |  | 2028-11-19 | Valid | 3985/PKTN.4.8/KHP/DL/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U33 | 33T4/00 | Fixed Roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | TU.5459/PKTN.4.5/DL/07/2025 | 2027-06-20 | Valid | 2027-11-20 | 062/SQ/SAU/XII/2023 | Valid | Valid |  | 2028-11-14 | Valid | 1351/PKTN.4.8/KHP/DL/05/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U32 | 32T4/00 | Fixed Roof | AVTUR | Prioritas 2 | Operation | TU.1326/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2027-11-20 | 060/SQ/SAU/XII/2023 | Valid | Overdue < 3 Tahun |  | 2030-03-20 | Valid | 1106/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U33 | 33T1/00 | Fixed Roof | HGO | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0075/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U33 | 33T7/00 | Fixed Roof | SOLAR | Prioritas 2 | Operation | TU.1377/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-28 | Valid | 2027-11-20 | 065/SQ/SAU/XII/2023 | Valid | Valid |  | 2033-10-05 | Valid | TU.3772/PKTN.4.5/KHP/DL/11/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U33 | 33T8/00 | Fixed Roof | SOLAR | Prioritas 2 | Operation | TU.5465/PKTN.4.5/DL/07/2025 | 2027-06-20 | Valid | 2027-11-20 | 066/SQ/SAU/XII/2023 | Valid | Valid |  | 2031-05-31 | Valid | 2291/PKTN.4.8/KHP/DL/06/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U34 | 34T1/00 | Fixed Roof | MFO | Prioritas 2 | Operation | TU.1857/PKTN.4.5/KHP/DL/03/2025 | 2027-02-21 | Valid | 2027-11-20 | 067/SQ/SAU/XII/2023 | Valid | Valid |  | 2028-11-20 | Valid | 3987/PKTN.4.8/KHP/DL/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U34 | 34T2/00 | Fixed Roof | MFO | Prioritas 2 | Operation | TU.2854/PKTN.4.5/DL/04/2025 | 2027-03-28 | Valid | 2027-11-20 | 068/SQ/SAU/XII/2023 | Valid | Valid |  | 2028-10-24 | Valid | 3993/PKTN.4.8/KHP/DL/11/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U33 | 33T2/00 | Fixed Roof | HGO | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0076/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Korosi dan deformasi menyebabkan air menggenang (kedalaman ±10cm) disekitar rolling ladder | Telah dilakukan perbaikan temporer dengan metode FRP | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U33 | 33T5/00 | Fixed Roof | Solar/HSD/MGO/ADO | Prioritas 2 | Operation | TU.5468/PKTN.4.5/DL/07/2025 | 2027-06-20 | Valid | 2027-11-20 | 063/SQ/SAU/XII/2023 | Valid | Overdue > 3 tahun |  | 2028-10-25 | Valid | 3996/PKTN.4.8/KHP/DL/11/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U33 | 33T6/00 | Fixed Roof | Solar/HSD/MGO/ADO | Prioritas 2 | Overhaul/Cleaning | TU.1327/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2027-11-20 | 064/SQ/SAU/XII/2023 | Valid | Overdue > 3 tahun |  | 2028-10-26 | Valid | 3999/PKTN.4.8/KHP/DL/11/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U35 | 35T1/00 | Fixed Roof | DCO | Prioritas 2 | Operation | TU.2855/PKTN.4.5/DL/04/2025 | 2027-03-28 | Valid | 2027-11-20 | 069/SQ/SAU/XII/2023 | Valid | Overdue > 3 tahun |  | 2030-03-20 | Valid | 1110/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Korosi dan deformasi menyebabkan air menggenang (kedalaman ±10cm) disekitar rolling ladder | Telah dilakukan perbaikan temporer dengan metode FRP | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U35 | 35T2/00 | Fixed Roof | LONG RESIDUE | Prioritas 3 | Overhaul/Cleaning | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-11-20 | 0139/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U36 | 36T102/00 | Floating Roof | PERTALITE | Prioritas 1 | Operation | T.3561/PKTN.4.5/DL/05/2025 | 2027-04-18 | Valid | 2028-10-19 | 00335/TNK/DW/IV/2025 | Valid | Valid |  | 2031-04-18 | Valid | T.3671/PKTN.4.5/DL/05/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U35 | 35T3/00 | Fixed Roof | MFO | Prioritas 2 | Operation | TU.6557/PKTN.4.5/DL/07/2025 | 2027-07-18 | Valid | 2027-11-20 | 070/SQ/SAU/XII/2023 | Valid | Overdue > 3 tahun |  | 2028-10-26 | Valid | 3997/PKTN.4.8/KHP/DL/11/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U35 | 35T4/00 | Fixed Roof | RFO | Prioritas 2 | Operation | TU.7323/PKTN.4.5/DL/08/2025 | 2027-08-08 | Valid | 2027-11-20 | 071/SQ/SAU/XII/2023 | Valid | Overdue > 3 tahun |  | 2028-10-29 | Valid | 4000/PKTN.4.8/KHP/DL/11/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U36 | 36T106/00 | Fixed Roof | NAPHTHA | Prioritas 1 | Operation | TU.5268/PKTN.4.5/DL/10/2024 | 2026-10-12 | Valid | 2027-11-20 | 0164/SQ/ST/XII/2023 | Valid | Valid |  | 2030-03-16 | Valid | 1118/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U37 | 37T101/00 | Fixed Roof | MFO | Prioritas 2 | Operation | TU.5262/PKTN.4.5/DL/10/2024 | 2026-10-12 | Valid | 2027-11-20 | 094/SQ/SAU/XII/2023 | Valid | Valid |  | 2030-03-16 | Valid | 1119/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U36 | 36T101/00 | Floating Roof | PERTALITE | Prioritas 1 | Operation | TU.2835/PKTN.4.5/DL/04/2025 | 2027-03-21 | Valid | 2027-11-20 | 091/SQ/SAU/XII/2023 | Valid | Overdue < 3 Tahun |  | 2032-04-22 | Valid | TU.1665/PKTN.4.8/KHP/DL/05/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Korosi dan deformasi menyebabkan air menggenang (kedalaman ±10cm) disekitar rolling ladder | Telah dilakukan perbaikan temporer dengan metode FRP | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U36 | 36T103/00 | Floating Roof | PERTALITE | Prioritas 1 | Operation | TU.2856/PKTN.4.5/DL/04/2025 | 2027-03-28 | Valid | 2027-11-20 | 092/SQ/SAU/XII/2023 | Valid | Overdue < 3 Tahun |  | 2031-05-23 | Valid | 2801/PKTN.4.8/KHP/DL/06/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Korosi dan deformasi menyebabkan air menggenang (kedalaman ±10cm) disekitar rolling ladder | Telah dilakukan perbaikan temporer dengan metode FRP | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U37 | 37T104/00 | Fixed Roof | LSWR | Prioritas 3 | Operation | TU.5264/PKTN.4.5/DL/10/2024 | 2026-10-12 | Valid | 2027-11-20 | 097/SQ/SAU/XII/2023 | Valid | Valid |  | 2032-04-22 | Valid | TU.1669/PKTN.4.8/KHP/DL/05/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U38 | 38T101/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Overhaul/Cleaning | 1483/PKTN.4.8/SKHP/DL/04/2022 | 2024-08-31 | Expired | 2027-11-20 | 098/SQ/SAU/XII/2023 | Valid | Valid |  | 2030-03-16 | Valid | 1120/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U36 | 36T105/00 | Floating Roof | HEAVY NAPHTHA | Prioritas 1 | Operation | TU.2857/PKTN.4.5/DL/04/2025 | 2027-03-28 | Valid | 2027-11-20 | 093/SQ/SAU/XII/2023 | Valid | Overdue < 3 Tahun |  | 2032-04-25 | Valid | TU.1668/PKTN.4.8/KHP/DL/05/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional | Tidak semua valve terpasang MOV |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U37 | 37T102/00 | Fixed Roof | MFO Low Sulphur 180 CST | Prioritas 2 | Operation | TU.5676/PKTN.4.5/DL/11/2024 | 2026-09-28 | Valid | 2027-11-20 | 095/SQ/SAU/XII/2023 | Valid | Overdue > 3 tahun |  | 2028-11-20 | Valid | 3986/PKTN.4.8/KHP/DL/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U38 | 38T104/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.2779/PKTN.4.5/SKHP/DL/08/2023 | 2027-06-20 | Valid | 2027-11-20 | 101/SQ/SAU/XII/2023 | Valid | Valid |  | 2030-03-20 | Valid | 1115/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | 50% non-functional | Under Perform | Proses pengadaan material | Good | Functional | tidak pernah di operasikan |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U37 | 37T103/00 | Fixed Roof | LSWR | Prioritas 3 | Overhaul/Cleaning | TU.1329/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2027-11-20 | 096/SQ/SAU/XII/2023 | Valid | Overdue > 3 tahun |  | 2028-11-22 | Valid | 1480/PKTN.4.8/KHP/DL/05/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good With Note | 50% non-functional | Indikasi kebocoran steam heater / kerusakan electric heater | Planning for internal cleanning, inspection, and Repair. Insolir inlet dan outlet steam/electric heater. | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T201/00 | Fixed Roof | LIGHT REFORMATE | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2026-12-19 | P005.NH.EW.002.23 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T202/00 | Fixed Roof | HEAVY REFORMATE | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2026-12-19 | P005.NH.EW.003.23 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T203/00 | Fixed Roof | EXTRACT | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2028-06-26 | E00024/AOBJAR | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T204/00 | Fixed Roof | BENZENE DAY TANK | Prioritas 1 | Operation | TU.4994/PKTN.4.5/DL/06/2026 | 2028-05-22 | Valid | 2028-06-26 | E00025/AOBJAR | Valid | Valid |  | 2034-03-31 | Valid | T.38/PKTN.4.5/DL/03/2024 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T205/00 | Fixed Roof | BENZENE DAY TANK | Prioritas 1 | Operation | T.81/PKTN.4.5/SKHP/DL/04/2024 | 2026-04-04 | Valid | 2028-06-26 | E00026/AOBJAR | Valid | Valid |  | 2034-03-31 | Valid | T.39/PKTN.4.5/DL/03/2024 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T206/00 | Fixed Roof | BENZENE | Prioritas 1 | Operation | TU.2858/PKTN.4.5/DL/04/2025 | 2027-03-28 | Valid | 2026-12-19 | P003.NH.EW.053.23 | Valid | Valid |  | 2030-03-20 | Valid | 1107/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U38 | 38T102/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.6553/PKTN.4.5/DL/07/2025 | 2027-07-18 | Valid | 2027-11-20 | 099/SQ/SAU/XII/2023 | Valid | Overdue > 3 tahun |  | 2032-03-29 | Valid | TU.1317/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Korosi dan deformasi menyebabkan air menggenang (kedalaman ±10cm) disekitar rolling ladder | Telah dilakukan perbaikan temporer dengan metode FRP | NA | NA |  |  | Good | Functional | tidak pernah di operasikan |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T208/00 | Fixed Roof | PAREX DAY TANK | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2026-12-19 | P003.NH.EW.004.23 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T209/00 | Fixed Roof | PAREX DAY TANK | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2026-12-19 | P003.NH.EW.005.23 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T210/00 | Fixed Roof | PARAXYLENE | Prioritas 1 | Operation | TU.6764/PKTN.4.5/DL/08/2025 | 2027-07-25 | Valid | 2026-12-19 | P003.NH.EW.055.23 | Valid | Valid |  | 2028-11-14 | Valid | 3977/PKTN.4.8/KHP/DL/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T211/00 | Fixed Roof | PARAXYLENE | Prioritas 1 | Operation | TU.2860/PKTN.4.5/DL/04/2025 | 2027-03-28 | Valid | 2026-12-19 | P003.NH.EW.056.23 | Valid | Valid |  | 2030-03-16 | Valid | 1121/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T212/00 | Fixed Roof | PARAXYLENE | Prioritas 1 | Operation | TU.6765/PKTN.4.5/DL/08/2025 | 2027-07-25 | Valid | 2026-12-19 | P003.NH.EW.057.23 | Valid | Valid |  | 2030-03-16 | Valid | 1122/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T213/00 | Fixed Roof | PARAXYLENE | Prioritas 1 | Operation | TU.2861/PKTN.4.5/DL/04/2025 | 2027-03-28 | Valid | 2026-12-19 | P003.NH.EW.058.23 | Valid | Valid |  | 2028-11-14 | Valid | 3976/PKTN.4.8/KHP/DL/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T1/00 | Fixed Roof | HVI-60 | Prioritas 3 | Operation | TU.3701/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2027-11-20 | 072/SQ/SAU/XII/2023 | Valid | Valid |  | 2033-05-31 | Valid | TU.1801/PKTN.4.5/KHP.DL/06/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T10/00 | Fixed Roof | SLOP | Prioritas 3 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0077/SQ/ST/X/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T11/00 | Fixed Roof | SPO RAFF | Prioritas 3 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0078/SQ/ST/X/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T12/00 | Fixed Roof | MINAREX-B | Prioritas 3 | Operation | TU.2828/PKTN.4.5/DL/04/2025 | 2027-03-21 | Valid | 2027-05-31 | 0079/SQ/ST/X/2023 | Valid | Valid |  | 2033-06-12 | Valid | TU. 1805/PKTN.4.5/KHP/DL/06/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T13/00 | Fixed Roof | SOLAR | Prioritas 3 | Operation | TU.3702/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2027-05-31 | 0080/SQ/ST/X/2023 | Valid | Valid |  | 2033-06-12 | Valid | TU. 1806/PKTN.4.5/KHP/DL/06/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T14/00 | Fixed Roof | SPO RAFF | Prioritas 3 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0081/SQ/ST/X/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T15/00 | Fixed Roof | LMO DIST | Prioritas 3 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0082/SQ/ST/X/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T16/00 | Fixed Roof | SPO DIST | Prioritas 3 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0083/SQ/ST/X/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T17/00 | Fixed Roof | MMO DIST | Prioritas 3 | Operation | TU.3705/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2027-05-31 | 0084/SQ/ST/X/2023 | Valid | Valid |  | 2033-08-12 | Valid | TU. 2822/PKTN.4.5/KHP/DL/06/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T18/00 | Fixed Roof | MMO DIST | Prioritas 3 | Operation | TU.3707/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2027-11-20 | 073/SQ/SAU/XII/2023 | Valid | Valid |  | 2033-08-12 | Valid | TU. 2821/PKTN.4.5/KHP/DL/06/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T19/00 | Fixed Roof | MDU SLOPS | Prioritas 3 | Operation | TU.1456/PKTN.4.5/SKHP/DL/04/2024 | 2026-04-03 | Valid | 2027-05-31 | 0085/SQ/ST/X/2023 | Valid | Valid |  | 2033-08-12 | Valid | TU. 2820/PKTN.4.5/KHP/DL/06/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T2/00 | Fixed Roof | HVI-60 | Prioritas 3 | Operation | Berita Acara Tera Ulang | 2027-04-10 | Valid | 2027-11-20 | 074/SQ/SAU/XII/2023 | Valid | Valid |  | 2031-05-31 | Valid | 2290/PKTN.4.8/KHP/DL/06/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T20/00 | Fixed Roof | HVI-60 | Prioritas 3 | Operation | TU.2832/PKTN.4.5/DL/04/2025 | 2027-03-21 | Valid | 2027-11-20 | 075/SQ/SAU/XII/2023 | Valid | Valid |  | 2028-10-23 | Valid | 3991/PKTN.4.8/KHP/DL/11/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T21/00 | Fixed Roof | HVI-95 | Prioritas 3 | Operation | TU.2829/PKTN.4.5/DL/04/2025 | 2027-03-21 | Valid | 2027-05-31 | 0086/SQ/ST/X/2023 | Valid | Valid |  | 2028-10-23 | Valid | 3992/PKTN.4.8/KHP/DL/11/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T22/00 | Fixed Roof | MINAREX-A | Prioritas 3 | Operation | TU.1458/PKTN.4.5/SKHP/DL/04/2024 | 2026-04-04 | Valid | 2027-05-31 | 0087/SQ/ST/X/2023 | Valid | Valid |  | 2028-10-24 | Valid | 3994/PKTN.4.8/KHP/DL/11/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T23/00 | Fixed Roof | MINAREX-A | Prioritas 3 | Operation | TU.1454/PKTN.4.5/SKHP/DL/04/2024 | 2026-04-03 | Valid | 2027-05-31 | 0088/SQ/ST/X/2023 | Valid | Valid |  | 2028-10-28 | Valid | 1315/PKTN.4.8/KHP/DL/04/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T3/00 | Fixed Roof | HVI-95 | Prioritas 3 | Operation | TU.1451/PKTN.4.5/SKHP/DL/04/2024 | 2026-04-02 | Valid | 2027-05-31 | 0092/SQ/ST/XII/2023 | Valid | Valid |  | 2028-10-27 | Valid | 1313/PKTN.4.8/KHP/DL/04/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T4/00 | Fixed Roof | HVI-95 | Prioritas 3 | Operation | BA Tera Ulang | 2027-04-30 | Valid | 2027-11-20 | 076/SQ/SAU/XII/2023 | Valid | Valid |  | 2028-10-24 | Valid | 3995/PKTN.4.8/KHP/DL/11/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U38 | 38T103/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.3700/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2027-11-20 | 100/SQ/SAU/XII/2023 | Valid | Overdue < 3 Tahun |  | 2031-05-24 | Valid | 2800/PKTN.4.8/KHP/DL/06/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional | tidak pernah di operasikan |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T6/00 | Fixed Roof | HVI-60 | Prioritas 3 | Overhaul/Cleaning | TU.1453/PKTN.4.5/SKHP/DL/04/2024 | 2026-04-02 | Valid | 2027-05-31 | 0093/SQ/ST/X/2023 | Valid | Valid |  | 2028-10-26 | Valid | 1312/PKTN.4.8/KHP/DL/04/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T7/00 | Fixed Roof | HVI-60 | Prioritas 3 | Operation | TU.1455/PKTN.4.5/SKHP/DL/04/2024 | 2026-04-03 | Valid | 2027-05-31 | 0094/SQ/ST/X/2023 | Valid | Valid |  | 2033-05-31 | Valid | TU.1803/PKTN.4.5/KHP.DL/06/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U39 | 39T207/00 | Fixed Roof | BENZENE | Prioritas 1 | Overhaul/Cleaning | TU.2859/PKTN.4.5/DL/04/2025 | 2027-03-28 | Valid | 2026-12-19 | P003.NH.EW.054.23 | Valid | Overdue > 3 tahun |  | 2030-03-20 | Valid | 1108/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U43 | 43T101/00 | Fixed Roof | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0113/SQ/ST/X/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional | tidak pernah di operasikan |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Pitting Corrosion | Perbaikan bottom plate tangki | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U43 | 43T102/00 | Fixed Roof | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0114/SQ/ST/X/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional | tidak pernah di operasikan |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U43 | 43T103/00 | Floating Roof | SLOP | Prioritas 2 | Operation | TU.5720/PKTN.4.5/DL/11/2024 | 2026-09-28 | Valid | 2027-05-31 | 0115/SQ/ST/X/2023 | Valid | Valid |  | 2033-03-01 | Valid | TU.1038/PKTN.4.5/KHP/DL/04/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional | tidak pernah di operasikan |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U43 | 43T2/00 | Fixed Roof | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0104/SQ/ST/X/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional | tidak pernah di operasikan |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U43 | 43T3/00 | Fixed Roof | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0105/SQ/ST/X/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional | tidak pernah di operasikan |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T8/00 | Fixed Roof | HVI-95 | Prioritas 3 | Overhaul/Cleaning | TU.2381/PKTN.4.5/DL/04/2025 | 2027-03-21 | Valid | 2027-05-31 | 0095/SQ/ST/X/2023 | Valid | Overdue < 3 Tahun |  | 2032-04-01 | Valid | TU.1314/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U46 | 46T1/00 | Floating Roof | BUFFER ME CR | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-11-20 | 0296/SQ/ST/XII/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U43 | 43T4/00 | Floating Roof | SLOP | Prioritas 2 | Overhaul/Cleaning | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0106/SQ/ST/X/2023 | Valid | Overdue > 3 tahun |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional | tidak pernah di operasikan |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | Belum terpasang krn perubahan design EFR > IFR > EFR |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T103/00 | Spherical Tank | LPG | Prioritas 1 | Operation | TU.6834/PKTN.4.5/DL/12/2024 | 2026-12-21 | Valid | 2030-02-10 | No. 0070-02-SMC/024/E02-L11/P1/2026 | Valid | Valid |  | 2030-03-31 | Valid | 0039/PKTN.4.7/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | Tidak seluruh valve menggunakan MOV |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T104/00 | Spherical Tank | LPG | Prioritas 1 | Operation | TU.4642/PKTN.4.5/SKHP/DL/12/2023 | 2025-11-30 | Valid | 2030-02-10 | No. 0071-02-SMC/024/E02-L11/P1/2026 | Valid | Valid |  | 2030-03-31 | Valid | 0040/PKTN.4.7/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | Tidak seluruh valve menggunakan MOV |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T501A/00 | Spherical Tank | LPG | Prioritas 1 | Operation | TU.1369/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-26 | Valid | 2028-06-04 | E00799/AOBJAR | Valid | Valid |  | 2037-11-09 | Valid | BA Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | Tidak seluruh valve menggunakan MOV |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T501B/00 | Spherical Tank | LPG | Prioritas 1 | Operation | TU.1330/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2028-06-04 | E00800/AOBJAR | Valid | Valid |  | 2026-11-30 | Valid | 276/SPK.5.8.21/S/DL/12/2014 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | Tidak seluruh valve menggunakan MOV |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T501C/00 | Spherical Tank | LPG | Prioritas 1 | Operation | TU.6832/PKTN.4.5/DL/12/2024 | 2026-12-21 | Valid | 2028-06-04 | E00801/AOBJAR | Valid | Valid |  | 2026-11-30 | Valid | 275/SPK.5.8.21/S/DL/12/2014 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | Tidak seluruh valve menggunakan MOV |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T511A/00 | Spherical Tank | PROPYLENE | Prioritas 1 | Operation | TU.1331/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2028-06-04 | E00802/AOBJAR | Valid | Valid |  | 2031-05-10 | Valid | BA Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | Tidak seluruh valve menggunakan MOV |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T511B/00 | Spherical Tank | PROPYLENE | Prioritas 1 | Operation | TU.1332/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2028-06-04 | E00803/AOBJAR | Valid | Valid |  | 2037-11-09 | Valid | BA Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | Tidak seluruh valve menggunakan MOV |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T511C/00 | Spherical Tank | PROPYLENE | Prioritas 1 | Operation | TU.1333/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2028-06-04 | E00804/AOBJAR | Valid | Valid |  | 2026-09-09 | Valid | BA Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | Tidak seluruh valve menggunakan MOV |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U46 | 46T2/00 | Floating Roof | BUFFER ME CR | Prioritas 1 | Overhaul/Cleaning | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-05-31 | 0108/SQ/ST/X/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | NA | NA |  |  | Good | Operational | Korosi |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T511E/00 | Spherical Tank | PROPYLENE | Prioritas 1 | Operation | TU.1370/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-26 | Valid | 2028-06-04 | E00806/AOBJAR | Valid | Valid |  | 2037-11-09 | Valid | BA Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | Tidak seluruh valve menggunakan MOV |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T511D/00 | Spherical Tank | PROPYLENE | Prioritas 1 | Operation | TU.6831/PKTN.4.5/DL/12/2024 | 2026-12-21 | Valid | 2028-06-04 | E00805/AOBJAR | Valid | Overdue < 3 Tahun |  | 2026-01-26 | Valid | BA Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-UTL | RU04-UTL -U57 | 57T2/00 | Fixed Roof | HEAVY GASOIL | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-11-20 | 0308/SQ/ST/XII/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U65 | 65T2/00 | Fixed Roof | BUNKER MFO | Prioritas 2 | Operation | TU.5462/PKTN.4.5/DL/07/2025 | 2027-06-20 | Valid | 2027-11-20 | 0141/SQ/ST/XII/2023 | Valid | Valid |  | 2028-11-22 | Valid | 2374/PKTN.4.8/KHP/DL/05/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T1/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.6766/PKTN.4.5/DL/08/2025 | 2027-07-25 | Valid | 2027-11-20 | 0144/SQ/ST/XII/2023 | Valid | Valid |  | 2033-10-19 | Valid | TU.3668/PKTN.4.5/KHP/DL/11/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage | Terdapat spot pitting pada lokasi 135° cw dari tangga |  | Good | Lifetime ≥ 3 years, no damage | Roof deck mengalami deformasi yang mengakibatkan air menggenang |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage | Korosi pada bagian cat yang mengelupas |  | Good | Lifetime ≥ 3 years, no damage | Korosi pada bagian cat yang mengelupas |  | Good | Functional | Valve outlet korosi |  | Good | <25% from standard, no significant settlement | Pondasi erosi |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T511F/00 | Spherical Tank | PROPYLENE | Prioritas 1 | Overhaul/Cleaning | TU.1334/PKTN.4.5/SKHP/DL/04/2024 | 2024-04-01 | Expired | 2028-06-04 | E00807/AOBJAR | Valid | Overdue < 3 Tahun |  | 2026-01-14 | Valid | BA Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T10/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.6768/PKTN.4.5/DL/08/2025 | 2027-07-25 | Valid | 2027-11-20 | 0145/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | 2030-03-16 | Valid | 1126/PKTN.4.8/KHP/DL/03/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T11/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.5673/PKTN.4.5/DL/11/2024 | 2026-09-28 | Valid | 2027-11-20 | 0146/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | 2033-11-16 | Valid | TU.4339/PKTN.4.5/KHP/DL/12/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  | Repair | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | Korosi dan deformasi menyebabkan air menggenang (±17cm) di roof deck, kondisi kotor oleh produk |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage | Kondisi baik, cat memudar |  | Good | Lifetime ≥ 3 years, no damage | Kondisi baik, cat memudar |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional | - | - | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T13/00 | Fixed Roof | BUNKER MFO | Prioritas 2 | Operation | Berita Acara 28/11/2025 | 2027-11-28 | Valid | 2027-11-20 | 081/SQ/SAU/XII/2023 | Valid | Valid |  | 2028-11-13 | Valid | 3974/PKTN.4.8/KHP/DL/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage | Kondisi kotor di sekitar lubang sampel |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good | handrail spot korosi |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T14/00 | Fixed Roof | BUNKER MFO | Prioritas 2 | Operation | TU.5461/PKTN.4.5/DL/07/2025 | 2027-06-20 | Valid | 2027-11-20 | 0148/SQ/ST/XII/2023 | Valid | Valid |  | 2029-01-25 | Valid | 384/PKTN.4.8/KHP/DL/02/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | Korosi |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | Kondisi baik, korosi di bagian cat yang memudar |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T12/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.6566/PKTN.4.5/DL/07/2025 | 2027-07-18 | Valid | 2027-11-20 | 0147/SQ/ST/XII/2023 | Valid | Overdue < 3 Tahun |  | 2031-05-31 | Valid | 1957/PKTN.4.8/KHP/DL/05/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage | Spot pitting di lokasi 90° cw |  | Good With Note | Reaching the end of lifetime within less than 3 years | Korosi dan deformasi menyebabkan air menggenang (kedalaman ±10cm) disekitar rolling ladder | Telah dilakukan perbaikan temporer dengan metode FRP | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage | Kondisi baik, korosi di beberapa titik |  | Good | Lifetime ≥ 3 years, no damage | Kondisi baik, korosi di beberapa titik |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Not Good | Damage causing hydrocarbon release. | Indikasi paparan gas HC dari Roof Seal | Penggantian Rim Seal Assy pada saat OH atau On stream | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T16/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.5460/PKTN.4.5/DL/07/2025 | 2027-06-20 | Valid | 2027-11-20 | 0150/SQ/ST/XII/2023 | Valid | Valid |  | 2028-11-12 | Valid | 3973/PKTN.4.8/KHP/DL/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good | Kondisi korosi ringan |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional | Korosi pada baut |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T15/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.3658/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2027-11-20 | 0149/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | 2033-11-16 | Valid | TU.4340/PKTN.4.5/KHP/DL/12/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage | Metal loss / pitting di shell course 1 dekat annular plate lokasi 135° cw |  | Good | Lifetime ≥ 3 years, no damage | Korosi (light to medium corroded) hampir di seluruh bagian dan deformasi di dekat area drain |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage | Pitting dekat annular lokasi 135° cw |  | Good | Lifetime ≥ 3 years, no damage | Pitting dekat annular lokasi 135° cw |  | Good | Functional | valve korosi pada baut |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T18/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.6769/PKTN.4.5/SKHP/DL/06/2023 | 2027-07-25 | Valid | 2027-11-20 | 082/SQ/SAU/XII/2023 | Valid | Valid |  | 2031-05-31 | Valid | 2288/PKTN.4.8/KHP/DL/06/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | Deformasi mengakibatkan genangan air di deck |  | Good | Functional |  |  | NA | NA | Valve korosi dan kotor |  | Good | Functional |  |  | Good | Good | Kondisi korosi Sebagian cat terkelupas |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T17/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.6559/PKTN.4.5/DL/07/2025 | 2027-07-18 | Valid | 2027-11-20 | 0151/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | 2032-04-22 | Valid | TU.1664/PKTN.4.8/KHP/DL/05/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good | Spiral ladder kondisi korosi, handrail cat memudar |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Not Good | Damage causing hydrocarbon release. | Indikasi paparan gas HC dari Roof Seal | Penggantian Rim Seal Assy pada saat OH atau On stream | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T19/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Overhaul/Cleaning | TU.6763/PKTN.4.5/DL/08/2025 | 2027-07-25 | Valid | 2027-11-20 | 0152/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | 2032-04-25 | Valid | TU.2770/PKTN.4.8/KHP/DL/08/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA | Valve korosi dan kotor |  | Good | Functional |  |  | Good | Good | Korosi, Sambungan Lasan Support To Shell di spiral ladder retak |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional | korosi pada valve dan baut |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T20/00 | Floating Roof | CRUDE OIL | Prioritas 1 | Operation | TU.3661/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2027-11-20 | 0154/SQ/ST/XII/2023 | Valid | Valid |  | 2033-07-11 | Valid | TU.2448/PKTN.4.5/KHP/DL/07/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | Beberapa lokasi deformasi menyebabkan air menggenang di roof deck |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | Crude Oil Leak |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | Crude Oil Leak |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional | - | - | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T3/00 | Floating Roof | Mix Crude Oil | Prioritas 1 | Operation | T.15/PKTN.4.5/KHP/DL/02/2024 | 2026-01-26 | Valid | 2028-05-28 | 2111.01.058.008.PJTM/2024 | Valid | Valid |  | 2030-03-31 | Valid | 1125/PKTN.4.8/KHP/DL/02/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T4/00 | Floating Roof | Mix Crude Oil | Prioritas 1 | Operation | TU.6833/PKTN.4.5/DL/12/2024 | 2026-12-21 | Valid | 2027-11-20 | 0157/SQ/ST/XII/2023 | Valid | Valid |  | 2032-11-22 | Valid | T.619/PKTN.4.5./KHP/DL/12/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T5/00 | Fixed Roof | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-11-20 | 0158/SQ/ST/XII/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T7/00 | Fixed Roof | BUNKER MFO | Prioritas 2 | Operation | TU.3660/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2027-11-20 | 083/SQ/SAU/XII/2023 | Valid | Valid |  | 2031-05-31 | Valid | 2804/PKTN.4.8/KHP/DL/06/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | Korosi |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | Deformasi mengakibatkan genangan air di deck, spot korosi di welding joint dekat plate |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T8/00 | Floating Roof | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-11-20 | 0160/SQ/ST/XII/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional | Sudah dilakukan Penggantian |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T9/00 | Floating Roof | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-11-20 | 0161/SQ/ST/XII/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional | Sudah dilakukan Penggantian |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U75 | 75T102/00 | Fixed Roof | BOILER FUEL | Prioritas 2 | Idle | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2027-11-20 | 0168/SQ/ST/XII/2023 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U85 | 85T201/00 | Fixed Roof | CHEMICAL | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2026-12-19 | P005.NH.EW.024.23 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U85 | 85T202/00 | Fixed Roof | CHEMICAL | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2026-12-19 | P005.NH.EW.025.23 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good | Board desk platform korosi |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U88 | 88T201/00 | Fixed Roof | CHEMICAL | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2026-12-19 | P005.NH.EW.026.23 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good | Foot step dan top platform mengalami korosi dan beberapa bagian ada yang patah |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-KPC | RU04-KPC -U88 | 88T202/00 | Fixed Roof | CHEMICAL | Prioritas 1 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2026-12-19 | P005.NH.EW.027.23 | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-SRU | RU04-SRU -U91 | 91T401/00 | Fixed Roof | LEAN AMINE | Prioritas 1 | Operation | NA | NA | NA | 2026-12-19 | P005.NH.EW.028.23 | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard | Nilai hambatan Bonding No. 1, 3 dan 6 melebihi 5 ohm |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | 50% non-functional | Under Perform | Proses pengadaan material | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good With Note | Exceeding 50% from standard; settlement between D/50 and D/100 | Pondasi erosi ± 5cm posisi 90° cw dari tangga | Perbaikan Foundation | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Cracked at support columns over 50% | fireproofing area lantai ada yang ambles |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-SRU | RU04-SRU -U91 | 91T402/00 | Fixed Roof | AMINE MAKE UP | Prioritas 1 | Operation | NA | NA | NA | 2026-12-19 | P005.NH.EW.029.23 | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard | Nilai hambatan Bonding No. 2, 3 dan 5 melebihi 5 ohm |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Outside the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | 50% non-functional | Under Perform | Proses pengadaan material | NA | NA |  |  | NA | NA |  |  | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good With Note | Cracked at support columns over 50% | fireproofing area lantai ada yang ambles |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-SRU | RU04-SRU -U93 | 93T401/00 | Fixed Roof | SULFUR | Prioritas 1 | Operation | No ATG Attached | NA | Valid | 2026-12-19 | P005.NH.EW.030.23 | Valid | Valid |  | 2033-08-10 | Valid | T.112/PKTN.4.5/KHP/DL/08/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | GTO | GTO | 47T522/00 | Floating Roof | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2028-05-08 | No. E00819/AOBJAR | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | GTO | GTO | 47T571/00 | Floating Roof | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2028-05-08 | No. E00818/AOBJAR | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T2/00 | Floating Roof | Mix Crude Oil | Prioritas 1 | Operation | TU.6767/PKTN.4.5/DL/08/2025 | 2027-07-25 | Valid | 2027-11-20 | 0153/SQ/ST/XII/2023 | Valid | Overdue > 3 tahun |  | 2033-10-19 | Valid | TU.3670/PKTN.4.5/KHP/DL/11/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | Roof deck mengalami deformasi yang mengakibatkan air menggenang |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good | Korosi, cat memudar dan mengelupas |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional | korosi pada baut dan valve |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U47 | 47T105/00 | Spherical Tank | LPG | Prioritas 1 | Operation | TU.1376/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-28 | Valid | 2030-02-10 | No. 0072-02-SMC/024/E02-L11/P1/2026 | Valid | Valid |  | 2029-11-30 | Valid | 1723/PKTN.4.8/KHP/DL/05/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | Tidak seluruh valve menggunakan MOV |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | GTO | GTO | 47T501/00 | Fixed Roof | OIL COLLECTION | Prioritas 2 | Operation | NA | NA | NA | 2026-12-19 | P005.NH.EW.032.23 | Valid | Valid |  | 2037-11-14 | Valid | TU.14363/PKTN.4.5/DL/12/2025 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U31 | 31T101/00 | Floating Roof | NAPHTHA | Prioritas 1 | Overhaul/Cleaning | TU.5675/PKTN.4.5/DL/112024 | 2026-09-28 | Valid | 2027-11-20 | 0170/SQ/ST/XII/2023 | Valid | Valid |  | 2031-11-27 | Valid | 1126/PKTN.4.8/KHP/DL/12/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-SRU | RU04-SRU -U93 | 93T402/00 | Fixed Roof | SULFUR | Prioritas 1 | Operation | No ATG Attached | NA | Valid | 2026-11-10 | 01582/ALBJAP | Valid | Valid |  | 2032-11-11 | Valid | T.569/PKTN.4.8/DL/11/2022 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U71 | 71T21/00 | Floating Roof | HOMC | Prioritas 1 | Overhaul/Cleaning | TU.5457/PKTN.4.5/DL/07/2025 | 2027-06-20 | Valid | 2027-11-20 | 0155/SQ/ST/XII/2023 | Valid | Valid |  | 2028-11-12 | Valid | 3979/PKTN.4.8/KHP/DL/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U38 | 38T105/00 | Floating Roof | Mix Crude | Prioritas 1 | Operation | TU.3659/PKTN.4.5/DL/09/2024 | 2026-08-31 | Valid | 2025-05-20 | E00808/AOBJAR | Valid | Overdue > 3 tahun |  | 2032-03-30 | Valid | TU.1310/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage | Thinning korosi pada roof | Dilakukan wrapping dan repainting roof | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Functional | Tidak seluruh valve menggunakan MOV |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | UTL-RFCC | UTL-RFCC | 165T501/00 | Fixed Roof | SPENT CAUSTIC | Prioritas 2 | Operation | NA | NA | NA | 2028-04-29 | No. E00820/AOBJAR | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | UTL-RFCC | UTL-RFCC | 110T501/00 | Fixed Roof | CAUSTIC | Prioritas 2 | Operation | NA | NA | NA | 2028-04-26 | No. E00828/AOBJAR | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | GTO | GTO | 107T501/00 | Fixed Roof | SLOP | Prioritas 2 | Operation | NA | NA | NA | 2028-05-08 | No. E00829/AOBJAR | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | GTO | GTO | 106T501/00 | Fixed Roof | MDEA | Prioritas 2 | Operation | NA | NA | NA | 2028-05-08 | No. E00830/AOBJAR | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RFCC | RFCC | 103T501/00 | Fixed Roof | COS SOLVENT | Prioritas 2 | Operation | NA | NA | NA | 2028-04-26 | No. E00831/AOBJAR | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T101/00 | Fixed Roof | HVI-95 | Prioritas 3 | Operation | TU.3711/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2027-05-31 | 0119/SQ/ST/X/2023 | Valid | Overdue > 3 tahun |  | 2030-03-16 | Valid | 1123/PKTN.4.8/KHP/DL/03/2020 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U35 | 35T5/00 | Fixed Roof | MFO | Prioritas 2 | Operation | TU.3725/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2031-11-30 | 907/PKTN.4.8/KHP/DL/12/2021 | Valid | Valid |  | 2031-11-30 | Valid | 907/PKTN.4.8/KHP/DL/12/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T102/00 | Fixed Roof | HVI-95 | Prioritas 3 | Operation | TU.3727/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2027-05-31 | 0120/SQ/ST/X/2023 | Valid | Valid |  | 2031-05-20 | Valid | 2289/PKTN.4.8/KHP/DL/06/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U38 | 38T110/00 | Fixed Roof | BOILER FUEL | Prioritas 2 | Idle | Bebas Tera Ulang | Bebas Tera Ulang | Valid | 2028-05-20 | E00813/AOBJAR | Valid | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U43 | 43T7/00 | Fixed Roof | BITUMEN PAINT | Prioritas 2 | Idle | NA | NA | NA | 2027-05-31 | 0107/SQ/ST/X/2023 | Valid | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T103/00 | Fixed Roof | HVI-160S | Prioritas 3 | Operation | TU.3728/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2027-05-31 | 0121/SQ/ST/X/2023 | Valid | Valid |  | 2031-05-20 | Valid | 2286/PKTN.4.8/KHP/DL/06/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T104/00 | Fixed Roof | HVI-95 | Prioritas 3 | Operation | TU.3729/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2027-05-31 | 0122/SQ/ST/X/2023 | Valid | Valid |  | 2031-04-30 | Valid | 1932/PKTN.4.8/KHP/DL/05/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T105/00 | Fixed Roof | HVI-650 | Prioritas 3 | Operation | TU.3730/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2027-11-20 | 102/SQ/SAU/XII/2023 | Valid | Valid |  | 2031-04-30 | Valid | 1930/PKTN.4.8/KHP/DL/05/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T106/00 | Fixed Roof | HVI-650 | Prioritas 3 | Operation | TU.2785/PKTN.4.5/SKHP/DL/08/2023 | 2027-07-18 | Valid | 2027-11-20 | 103/SQ/SAU/XII/2023 | Valid | Valid |  | 2031-05-24 | Valid | 1975/PKTN.4.8/KHP/DL/05/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T107/00 | Fixed Roof | HVI-160S | Prioritas 3 | Operation | TU.3731/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2027-05-31 | 0123/SQ/ST/X/2023 | Valid | Valid |  | 2031-04-25 | Valid | 1933/PKTN.4.8/KHP/DL/05/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T108/00 | Fixed Roof | HVI-160S | Prioritas 3 | Operation | TU.3732/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2027-05-31 | 0124/SQ/ST/X/2023 | Valid | Valid |  | 2031-04-25 | Valid | 1934/PKTN.4.8/KHP/DL/05/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T109/00 | Fixed Roof | HVI-650 | Prioritas 3 | Operation | TU.0363/PKTN.4.5/DL/01/2025 | 2027-01-12 | Valid | 2027-11-20 | 104/SQ/SAU/XII/2023 | Valid | Valid |  | 2031-04-24 | Valid | 1929/PKTN.4.8/KHP/DL/05/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U35 | 35T6/00 | Fixed Roof | MFO | Prioritas 2 | Operation | TU.3726/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2025-10-26 | PTIA/21422/MT/01/2022 | Valid | Valid |  | 2031-11-30 | Valid | 908/PKTN.4.8/KHP/DL/12/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T110/00 | Fixed Roof | HVI-650 | Prioritas 3 | Operation | TU.3733/PKTN.4.5/DL/09/2024 | 2026-08-24 | Valid | 2027-05-31 | 0125/SQ/ST/X/2023 | Valid | Valid |  | 2031-05-20 | Valid | 2805/PKTN.4.8/KHP/DL/06/2021 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T111/00 | Fixed Roof | LMO RAFF | Prioritas 3 | Operation | TU.3709/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2027-05-31 | 0126/SQ/ST/X/2023 | Valid | Valid |  | NA | Valid | TU. 1449/PKTN.4.5/KHP/DL/06/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T113/00 | Fixed Roof | MMO RAFF | Prioritas 3 | Operation | TU.5265/PKTN.4.5/DL/09/2024 | 2026-10-12 | Valid | 2027-05-31 | 0128/SQ/ST/X/2023 | Valid | Valid |  | NA | Valid | TU. 2451/PKTN.4.5/KHP/DL/06/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Korosi dan deformasi menyebabkan air menggenang (kedalaman ±10cm) disekitar rolling ladder | Telah dilakukan perbaikan temporer dengan metode FRP | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LOC2 | LOC2 | 041T115/00 | Fixed Roof | SPO DIST | Prioritas 3 | Operation | TU.0362/PKTN.4.5/DL/01/2025 | 2027-01-12 | Valid | 2027-11-20 | 0130/SQ/ST/X/2023 | Valid | Valid |  | NA | Valid | TU.3309/PKTN.4.5/KHP/DL/09/2023 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T24/00 | Fixed Roof | DAO SLACK WAX | Prioritas 3 | Operation | TU.7325/PKTN.4.5/DL/08/2025 | 2027-08-08 | Valid | 2027-05-31 | 0089/SQ/ST/X/2023 | Valid | Valid |  | 2027-07-25 | Valid | TU.6586/PKTN.4.5/DL/07/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T25/00 | Fixed Roof | DAO SLACK WAX | Prioritas 3 | Operation | TU.3708/PKTN.4.5/DL/09/2024 | 2026-08-16 | Valid | 2027-05-31 | 0090/SQ/ST/X/2023 | Valid | Valid |  | 2031-08-08 | Valid | TU.7529/PKTN.4.5/DL/08/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 41T26/00 | Fixed Roof | LMO SLACK WAX | Prioritas 3 | Operation | TU.2872/PKTN.4.5/DL/04/2025 | 2027-03-28 | Valid | 2027-05-31 | 0091/SQ/ST/X/2023 | Valid | Valid |  | 2027-06-13 | Valid | TU.9582/PKTN.4.5/DL/09/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC3 | RU04-LOC3 -000 | 041T313/00 | Fixed Roof | ASPHALT-60/70 | Prioritas 3 | Operation | T.0115/PKTN.4.5/KN/01/2025 | 2027-01-01 | Valid | 2026-12-19 | P005.NH.EW.060.23 | Valid | Valid |  | 2031-01-31 | Valid | T.0256/PKTN.4.5/DL/01/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-LOC1 | RU04-LOC1 -000 | 24T2/00 | Fixed Roof | HVI-160 | Prioritas 3 | Idle | NA | NA | NA | NA | NA | NA | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | GTO | GTO | 47T572/00 | FIXED ROOF | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | NA | NA | NA | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | GTO | GTO | 47T573/00 | FLOATING ROOF | SLOP | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | NA | NA | NA | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U42 | 42T1/00 | FIXED ROOF | SHORT RESIDUE | Prioritas 3 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | NA | NA | NA | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U42 | 42T2/00 | FIXED ROOF | ASPHALT-60/70 | Prioritas 3 | Operation | Berita Acara 28/11/2025 | 2027-11-28 | Valid | NA | NA | NA | Valid |  | 2027-06-13 | Valid | TU.9574/PKTN.4.5/DL/09/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U42 | 42T3/00 | FIXED ROOF | ASPHALT-60/70 | Prioritas 3 | Operation | TU.1168/PKTN.4.5/KN/02/2025 | 2027-02-11 | Valid | 2027-11-20 | No. 079/SQ/SAU/XII/2023 | Valid | Valid |  | 2031-05-03 | Valid | T.3562/PKTN.4.5/DL/05/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U42 | 42T4/00 | FIXED ROOF | ASPHALT-60/70 | Prioritas 3 | Operation | TU.2060/PKTN.4.5/SKHP/DL/02/2026 | 2028-02-06 | Valid | 2027-05-01 | No. 0097/SQ/ST/X/2023 | Valid | Valid |  | 2027-06-13 | Valid | TU.9576/PKTN.4.5/DL/09/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U42 | 42T5/00 | FIXED ROOF | ASPHALT-60/70 | Prioritas 3 | Operation | Berita Acara 28/11/2025 | 2027-11-28 | Valid | NA | NA | NA | Valid |  | 2027-06-13 | Valid | TU.9577/PKTN.4.5/DL/09/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U42 | 42T6/00 | FIXED ROOF | ASPHALT-60/70 | Prioritas 3 | Operation | TU.4639/PKTN.4.5/SKHP/DL/12/2023 | 2025-11-30 | Valid | NA | NA | NA | Valid |  | 2027-06-13 | Valid | TU.9578/PKTN.4.5/DL/09/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U42 | 42T7/00 | FIXED ROOF | LMO SLACK WAX | Prioritas 3 | Operation | TU.2827/PKTN.4.5/DL/04/2025 | 2027-03-21 | Valid | NA | NA | NA | Valid |  | 2027-06-13 | Valid | TU.9579/PKTN.4.5/DL/09/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U42 | 42T8/00 | FIXED ROOF | SHORT RESIDUE | Prioritas 3 | Operation | TU.4640/PKTN.4.5/SKHP/DL/12/2023 | 2025-11-30 | Valid | NA | NA | NA | Valid |  | 2027-06-13 | Valid | TU.9580/PKTN.4.5/DL/09/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U42 | 42T9/00 | FIXED ROOF | ASPHALT-60/70 | Prioritas 3 | Overhaul/Cleaning | Berita Acara 28/11/2025 | 2027-11-28 | Valid | NA | NA | NA | Overdue > 3 tahun |  | 2027-06-13 | Valid | TU.9581/PKTN.4.5/DL/09/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U42 | 42T10/00 | FIXED ROOF | ASPHALT-60/70 | Prioritas 3 | Operation | TU.1481/PKTN.4.5/SKHP/DL/5/2024 | 2026-05-03 | Valid | 2028-06-18 | No. 0098-02-SMC/052-23/E08-L11/P1/2024 | Valid | Valid |  | 2034-05-31 | Valid | T.85/PKTN.4.5/KHP/DL/05/2024 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML -U43 | 43T1/00 | FIXED ROOF | LONG RESIDUE | Prioritas 3 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | NA | NA | NA | Overdue > 3 tahun |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U49 | 49T1/00 | FIXED ROOF | PEN BITUMEN | Prioritas 2 | Operation | NA | NA | NA | NA | NA | NA | Valid |  | 2032-11-01 | Valid | T.618/PKTN.4.5/KHP/DL/XII/2022 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-TRML | RU04-TRML-U49 | 49T2/00 | FIXED ROOF | PEN BITUMEN | Prioritas 2 | Operation | No ATG Attached | NA | Valid | 2027-05-31 | No. 0110/SQ/ST/X/2023 | Valid | Valid |  | 2028-11-14 | Valid | 2373/PKTN.4.8/KHP/DL/05/2019 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-UTL | UTL-EXISTING | 43T6/00 | FIXED ROOF | Fuel Oil Tank | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | NA | NA | NA | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-UTL | RU04-UTL -U57 | 57T1/00 | FIXED ROOF | Fuel Oil Tank | Prioritas 2 | Operation | Bebas Tera Ulang | Bebas Tera Ulang | Valid | NA | NA | NA | Valid |  | Bebas Tera Ulang | Valid | Bebas Tera Ulang | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | UTL-RFCC | RU04-TRML-U157 | 157T501/00 | FIXED ROOF | Fuel Oil Tank | Prioritas 2 | Operation | NA | NA | NA | NA | NA | NA | Valid |  | NA | Valid | TU.9521/PKTN.4.5/DL/09/2025 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LNHT-ISOM | LNHT-ISOM | 100T622/00 | FIXED ROOF | CAUSTIC | Prioritas 2 | Operation | NA | NA | NA | NA | NA | NA | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LNHT-ISOM | LNHT-ISOM | 100T623/00 | FIXED ROOF | CAUSTIC | Prioritas 2 | Operation | NA | NA | NA | NA | NA | NA | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | LNHT-ISOM | LNHT-ISOM | 100T631/00 | FIXED ROOF | SPENT CAUSTIC | Prioritas 2 | Operation | NA | NA | NA | NA | NA | NA | Valid |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU IV Cilacap | RU04-FOC1 | FOC1 | 08T102/00 | Fixed roof | CAUSTIC | Prioritas 2 | Operation | NA | NA | NA | NA | NA | NA | Overdue > 3 tahun |  | NA | NA | NA | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good With Note | Outside the range of -0.85 to -1.5 V | Cathodic Underprotection | Akan dilakukan assesment terkait cathodic protection | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -LAWE | 101-5-T-01A/00 | Floating roof | Mix Crude Oil | Prioritas 1 | Operation | TU.3351/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-21 | Valid | 2029-01-21 | P006.NH.STH.062.25 | Valid | Valid |  | 2032-03-18 | Valid | T.244/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional | Leak pada line foam chamber | Perbaikan menggunakan kontrak spot pemadam, foam dan sprinkler tangki lawe-lawe, Target eksekusi September 2025 | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -LAWE | 101-5-T-01B/00 | Floating roof | Mix Crude Oil | Prioritas 1 | Operation | TU.3346/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-20 | Valid | 2029-01-21 | P006.NH.STH.063.25 | Valid | Valid |  | 2029-04-13 | Valid | 1452/PKTN.4.8/KHP/DL/05/2019 | Good | All functional | NA | NA | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Not Good | Non-functional | Tidak berfungsi | Material baru FGDS sudah tiba, i/p pengecekan engineer | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -LAWE | 101-5-T-01C/00 | Floating roof | Mix Crude Oil | Prioritas 1 | Overhaul/Cleaning | TU.3352/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-21 | Valid | 2027-05-25 | P006.NH.SA.110.23 | Valid | Overdue > 3 tahun |  | 2029-04-15 | Valid | 1453/PKTN.4.8/KHP/DL/05/2019 | Good | All functional | NA | NA | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good With Note | 50% non-functional | Bocoran pada clamp pipeline 4" sprinkle | Perbaikan line | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -LAWE | 101-5-T-01D/00 | Floating roof | Mix Crude Oil | Prioritas 1 | Operation | TU.3347/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-20 | Valid | 2027-05-25 | P006.NH.SA.111.23 | Valid | Overdue > 3 tahun |  | 2032-02-19 | Valid | TU.885/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard |  |  | NA | NA | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional | Tidak berfungsi | Material baru FGDS sudah tiba, i/p pengecekan engineer | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -LAWE | 101-5-T-01E/00 | Floating roof | Mix Crude Oil | Prioritas 1 | Operation | TU.2272/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2027-05-25 | P006.NH.SA.112.23 | Valid | Valid |  | 2030-10-18 | Valid | 3129/PKTN.4.8/KHP/DL/11/2020 | Good | All functional | NA | NA | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  | NA | Good | Functional | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | Good With Note | 50% non-functional | Leak pada line foam chamber | Perbaikan menggunakan kontrak spot pemadam, foam dan sprinkler tangki lawe-lawe, Target eksekusi September 2025 | Good | Functional |  |  | Good | Functional | Tidak berfungsi | Material baru FGDS sudah tiba, i/p pengecekan engineer | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good With Note | Some non-functional but not leaking | Weather shield sebagian renggang dan Rim Seal renggang ± 8-10 cm | Penggantian rim seal dan perbaikan weather shield | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -LAWE | 101-5-T-01F/00 | Floating roof | Mix Crude Oil | Prioritas 1 | Operation | TU.2270/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-13 | Valid | 2027-05-25 | P006.NH.SA.113.23 | Valid | Valid |  | 2033-11-26 | Valid | TU.3884/PKTN.4.5/KHP/DL/11/2023 | Good | All functional | NA | NA | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good With Note | 50% non-functional | Bocoran pada line 6" sprinkle | Perbaikan line | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -LAWE | 101-5-T-01G/00 | Floating roof | Mix Crude Oil | Prioritas 1 | Operation | TU.2271/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-13 | Valid | 2029-01-21 | P006.NH.STH.003.25 | Valid | Valid |  | 2033-09-06 | Valid | TU.2175/PKTN.4.5/KHP/DL/07/2023 | Good | All functional | NA | NA | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good With Note | 50% non-functional | Leak pada line foam chamber | Perbaikan menggunakan kontrak spot pemadam, foam dan sprinkler tangki lawe-lawe, Target eksekusi September 2025 | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-01/00 | Fixed roof | Mix Crude Oil | Prioritas 1 | Operation | TU.0660/PKTN.4.5/DL/02/2025 | 2027-01-27 | Valid | 2027-05-25 | P006.NH.SA.063.23 | Valid | Valid |  | 2029-11-15 | Valid | TU.3442/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | NA | NA | Good | Standard | NA | NA | Good | Standard | NA | NA | Good | Functional | NA | NA | NA | NA | Tidak masuk list PM IHLA | NA | Good | Functional |  | NA | Good | Functional | Tidak masuk list PM IHLA | NA | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-02/00 | Fixed roof | Mix Crude Oil | Prioritas 1 | Operation | TU.1489/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-07 | Valid | 2029-01-21 | P006.NH.STH.004.25 | Valid | Valid |  | 2030-11-18 | Valid | 3807/PKTN.4.8/KHP/DL/12/2020 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | NA | NA | Tidak masuk list PM IHLA | NA | Good | Functional |  | NA | Good | Functional | Tidak masuk list PM IHLA | NA | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-03/00 | Fixed roof | Mix Crude Oil | Prioritas 1 | Operation | TU.4392/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2027-05-25 | P006.NH.SA.064.23 | Valid | Valid |  | 2029-01-29 | Valid | TU.973/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-04/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.4393/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.005.25 | Valid | Overdue < 3 tahun |  | 2029-10-06 | Valid | TU.2034/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-05/00 | Fixed roof | SOLAR | Prioritas 2 | Overhaul/Cleaning | TU.3516/PKTN.4.5/SKHP/DL/11/2022 | 2024-10-22 | Expired | 2024-06-12 | 1104-02-BPC/293/E08-L11/P1/2020-02 | Expired | Valid |  | 2029-11-14 | Valid | 4548/PKTN.4.8/KHP/DL/12/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-06/00 | Fixed roof | SOLAR | Prioritas 2 | Overhaul/Cleaning | TU.3345/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-19 | Valid | 2024-06-24 | 1104-02-BPC/293/E08-L11/P1/2020-47 | Expired | Valid |  | 2024-05-20 | Valid | TU.1824/PKTN.4.8/KHP/DL/05/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-07/00 | Fixed roof | PERTAMAX | Prioritas 1 | Overhaul/Cleaning | SKHP TU.0895-PKTN.4.5-KN-02-2025 | 2027-02-07 | Valid | 2024-06-28 | 1104-02-BPC/293/E08-L11/P1/2020-03 | Expired | Valid |  | 2032-11-30 | Valid | T.624/PKTN.4.5/KHP/DL/12/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-15/00 | Fixed roof | Mix Crude Oil | Prioritas 1 | Operation | TU,1351/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-24 | Valid | 2027-05-25 | P006.NH.SA.065.23 | Valid | Valid |  | 2033-12-09 | Valid | TU.3208/PKTN.4.5/KHP/DL/09/2023 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | NA | NA | Tidak masuk list PM IHLA | NA | Good | Functional |  | NA | Good | Functional | Tidak masuk list PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-16/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.2311/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2030-06-28 | 1104-02-BPC/293/E08-L11/P1/2020-48 | Valid | Valid |  | 2032-11-29 | Valid | T.625/PKTN.4.5/KHP/DL/12/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-17/00 | Fixed roof | SOLAR | Prioritas 2 | Overhaul/Cleaning | TU.3526/PKTN.4.5/SKHP/DL/11/2022 | 2024-10-24 | Expired | 2024-06-16 | 1104-02-BPC/293/E08-L11/P1/2020-04 | Expired | Valid |  | 2029-01-25 | Valid | 387/PKTN.4.8/KHP/DL/02/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-18/00 | Fixed roof | RESIDUE | Prioritas 3 | Operation | TU.4406/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2024-06-16 | 1104-02-BPC/293/E08-L11/P1/2020-49 | Expired | Valid |  | 2031-10-13 | Valid | 3618/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-19/00 | Fixed roof | RESIDUE | Prioritas 3 | Operation | TU.2312/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2029-01-21 | P006.NH.STH.007.25 | Valid | Valid |  | 2033-12-09 | Valid | T.135/PKTN.4.5/KHP/DL/09/2023 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-20/00 | Fixed roof | DIESEL | Prioritas 2 | Operation | TU,1352/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-24 | Valid | 2029-01-21 | P006.NH.STH.008.25 | Valid | Valid |  | 2029-08-18 | Valid | T.243/PKTN.4.8/KHP/DL/03/2022 | Good | All functional |  |  | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional | Perbaikan Selesai |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-21/00 | Fixed roof | PERTALITE | Prioritas 1 | Overhaul/Cleaning | TU.496/PKTN.4.5/SKHP/DL/02/2023 | 2025-02-07 | Expired | 2027-05-25 | P006.NH.SA.066.23 | Valid | Valid |  | 2031-10-14 | Valid | 3619/PKTN.4.8/KHP/DL/10/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-22/00 | Fixed roof | PERTAMAX | Prioritas 1 | Operation | TU.4394/PKTN.4.5/DL/10/2024 | 2026-09-27 | Expired | 2029-01-21 | P006.NH.STH.009.25 | Valid | Overdue > 3 tahun |  | 2032-04-06 | Valid | TU.2032/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-23/00 | Fixed roof | PERTALITE | Prioritas 1 | Operation | TU.4395/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.010.25 | Valid | Overdue > 3 tahun |  | 2031-10-03 | Valid | 1122/PKTN.4.8/KHP/DL/03/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-24/00 | Fixed roof | HOMC 92 | Prioritas 1 | Operation | TU.4396/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.011.25 | Valid | Overdue > 3 tahun |  | 2034-02-23 | Valid | TU. 818/PKTN.4.5/SKHP/DL/03/2024 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-25/00 | Fixed roof | AVTUR | Prioritas 2 | Operation | TU.3519/PKTN.4.5/SKHP/DL/11/2022 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.012.25 | Valid | Valid |  | 2033-03-17 | Valid | TU.50/PKTN.4.5/KHP/DL/03/2023 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional | OH Tank / Cleaning Tank | NA | Good | Functional |  | NA | Good | Functional | OH Tank / Cleaning Tank | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-26/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TTU.0661/PKTN.4.5/DL/02/2025 | 2027-01-27 | Valid | 2029-01-21 | P006.NH.STH.013.25 | Valid | Valid |  | 2033-11-16 | Valid | TU.4446/PKTN.4.5/KHP/DL/12/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-27/00 | Fixed roof | AVTUR | Prioritas 2 | Operation | TU.4398/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.014.25 | Valid | Valid |  | 2032-04-06 | Valid | TU.2031/PKTN.4.8/KHP/DL/06/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-28/00 | Fixed roof | KEROSENE | Prioritas 2 | Overhaul/Cleaning | TU.3522/PKTN.4.5/SKHP/DL/11/2022 | 2024-10-24 | Expired | 2024-06-22 | 1104-02-BPC/293/E08-L11/P1/2020-07 | Expired | Valid |  | 2030-10-20 | Valid | 3130/PKTN.4.8/KHP/DL/10/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-29/00 | Fixed roof | PERTAMAX | Prioritas 1 | Operation | TU.2313/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2029-01-21 | P006.NH.STH.015.25 | Valid | Valid |  | 2032-02-04 | Valid | T.287/PKTN.4.5/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-30/00 | Fixed roof | PERTALITE | Prioritas 1 | Overhaul/Cleaning | TU.3523/PKTN.4.5/SKHP/DL/11/2022 | 2024-10-24 | Expired | 2024-06-17 | 1104-02-BPC/293/E08-L11/P1/2020-09 | Expired | Valid |  | 2024-02-26 | Valid | 652/PKTN 4.8/KHP/DL/03/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  | TUNGGU PENYELESAIAN MOD TANK KPB | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-31/00 | Floating roof | PERTALITE | Prioritas 1 | Overhaul/Cleaning | TU.1487/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-07 | Valid | 2027-05-25 | P006.NH.SA.070.23 | Valid | Overdue > 3 tahun |  | 2031-11-03 | Valid | 1121/PKTN.4.8/KHP/DL/03/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good With Note | 50% non-functional | Fire Suppresion tidak berfungsi | Perbaikan | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good With Note | Damaged but not yet causing hydrocarbon release. | Rim seal Gap & weather seal Dent/bengkok | Perbaikan menggunakan Kontrak Spot | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-32/00 | Floating roof | HOMC 92 | Prioritas 1 | Operation | TU.1488/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-07 | Valid | 2027-05-25 | P006.NH.SA.071.23 | Valid | Valid |  | 2031-08-13 | Valid | 2987/PKTN.4.8/KHP/DL/09/2021 | Good | All functional | NA | NA | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good With Note | 50% non-functional | Fire Suppresion tidak berfungsi | Perbaikan | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good With Note | Damaged but not yet causing hydrocarbon release. | Rim seal Gap & weather seal Dent/bengkok | Perbaikan menggunakan Kontrak Spot | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | A-33/00 | Floating roof | PERTALITE | Prioritas 1 | Operation | TU.2273/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2028-01-31 | P021.NH.SA.001.24 | Valid | Valid |  | 2032-04-19 | Valid | TU.1440/PKTN.4.8/KHP/DL/04/2022 | Good | All functional | NA | NA | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional | Perbaikan Selesai |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good With Note | Damaged but not yet causing hydrocarbon release. | Rim seal Gap & weather seal Dent/bengkok | Perbaikan menggunakan Kontrak Spot | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | C-20-01A/00 | Spherical Tank | LPG | Prioritas 3 | Operation | TU,1357/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-27 | Valid | 2029-01-21 | P006.NH.STH.016.25 | Valid | Valid |  | 2029-12-31 | Valid | 121/SPK.5.8.16/S/DL/08/2014 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | C-20-01B/00 | Spherical Tank | LPG | Prioritas 3 | Operation | TU.3350/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-21 | Valid | 2029-01-21 | P006.NH.STH.017.25 | Valid | Valid |  | 2032-12-11 | Valid | 0642/25/EX/12/2022 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-01A/00 | Floating roof | Mix Crude Oil | Prioritas 1 | Operation | TU.590/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-08 | Valid | 2027-05-25 | P006.NH.SA.072.23 | Valid | Valid |  | 2032-04-09 | Valid | TU.3445/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional | Tidak masuk list PM IHLA; Modifikasi Tank by KPB | NA | Good | Functional |  | NA | Good | Functional | Tidak masuk list PM IHLA; Modifikasi Tank by KPB | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-01B/00 | Floating roof | Mix Crude Oil | Prioritas 1 | Operation | TU.591/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-08 | Valid | 2027-05-25 | P006.NH.SA.073.23 | Valid | Valid |  | 2029-01-29 | Valid | 390/PKTN.4.8/KHP/DL/02/2019 | Good | All functional | NA | NA | Good | Standard | - |  | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional | OH Tank / Cleaning Tank | NA | Good | Functional |  | NA | Good | Functional | OH Tank / Cleaning Tank | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-03/00 | Fixed roof | SWEET NAPHTA | Prioritas 1 | Operation | TU.592/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-08 | Valid | 2027-05-25 | P006.NH.SA.074.23 | Valid | Valid |  | 2033-09-13 | Valid | T.136/PKTN.4.5/KHP/DL/09/2023 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-04A/00 | Fixed roof | HVGO | Prioritas 3 | Operation | TU.2320/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2027-05-25 | P006.NH.SA.075.23 | Valid | Valid |  | 2033-11-23 | Valid | TU.4448/PKTN.4.5/KHP/DL/12/2023 | Good | All functional | CLEANING OH TANK | Menunggu selesai cleaning/OH Tank | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-04B/00 | Fixed roof | HVGO | Prioritas 3 | Operation | TU.2266/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-11 | Valid | 2027-05-25 | P006.NH.SA.076.23 | Valid | Valid |  | 2025-03-17 | Valid | TU.752/PKTN.4.5/KHP/DL/03/2023 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-04C/00 | Fixed roof | HVGO | Prioritas 3 | Operation | TU.2267/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-11 | Valid | 2027-05-25 | P006.NH.SA.077.23 | Valid | Valid |  | 2025-03-17 | Valid | TU.753/PKTN.4.5/KHP/DL/03/2023 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-05A/00 | Floating roof | NAPHTA | Prioritas 1 | Operation | TU.2265/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-10 | Valid | 2027-05-25 | P006.NH.SA.078.23 | Valid | Valid |  | 2032-04-09 | Valid | TU.3444/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | CLEANING OH TANK | Menunggu selesai cleaning/OH Tank | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | - | - | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good With Note | Some non-functional but not leaking | Weather shield terlipat dan rim seal 2/3 dari keliling kempot | Penggantian rim seal dan perbaikan weather shield | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good With Note | Damaged but not yet causing hydrocarbon release. | Rim seal Gap & weather seal Dent/bengkok | Perbaikan menggunakan Kontrak Spot | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-05B/00 | Floating roof | KEROSENE | Prioritas 2 | Operation | TU.2268/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-12 | Valid | 2027-05-25 | P006.NH.SA.079.23 | Valid | Valid |  | 2032-08-31 | Valid | TU.3450/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | NA | NA | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-05C/00 | Floating roof | NAPHTA | Prioritas 1 | Operation | TU.2317/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2029-01-21 | P006.NH.STH.018.25 | Valid | Valid |  | 2028-11-23 | Valid | 1173/PKTN.4.8/KHP/DL/12/2018 | Good | All functional | NA | NA | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-05D/00 | Floating roof | KEROSENE | Prioritas 2 | Operation | TU.1486/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-07 | Valid | 2029-01-21 | P006.NH.STH.019.25 | Valid | Valid |  | 2030-02-27 | Valid | 505/PKTN.4.8/KHP/DL/02/2020 | Good | All functional | NA | NA | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-06A/00 | Floating roof | REFORMATE | Prioritas 1 | Operation | 859/PKTN.4.8/KHP/DL/08/2019 | 2021-08-12 | Expired | 2029-01-21 | 0641-02-BPC/1681/e08-L11/P1/2023-03 | Valid | Valid |  | 2029-11-11 | Valid | 1657/PKTN.4.8/KHP/DL/12/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-06B/00 | Floating roof | REFORMATE | Prioritas 1 | Operation | TU.593/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-08 | Valid | 2029-01-21 | P006.NH.STH.020.25 | Valid | Valid |  | 2030-10-11 | Valid | 3501/PKTN.4.8/KHP/DL/12/2020 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good With Note | Damaged but not yet causing hydrocarbon release. | Rim seal Gap & weather seal Dent/bengkok | Perbaikan menggunakan Kontrak Spot | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-07A/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.2319/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2027-05-25 | P006.NH.SA.080.23 | Valid | Valid |  | 2033-11-16 | Valid | TU.4445/PKTN.4.5/KHP/DL/12/2023 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-07B/00 | Fixed roof | SOLAR | Prioritas 2 | Overhaul/Cleaning | TU.1483/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-06 | Valid | 2029-01-21 | P006.NH.STH.021.25 | Valid | Overdue < 3 tahun |  | 2032-02-09 | Valid | TU.3448/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | CLEANING OH TANK | Menunggu selesai cleaning/OH Tank | Good | Standard | OH Tank | Tunggu Penyelesaian OH Tank | Good | Standard | OH Tank | Tunggu Penyelesaian OH Tank | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-07C/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.1484/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-06 | Valid | 2027-05-25 | P006.NH.SA.081.23 | Valid | Valid |  | 2030-01-24 | Valid | 503/PKTN.4.8/KHP/DL/02/2020 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-08/00 | Fixed roof | PERTADEX | Prioritas 2 | Operation | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2028-01-31 | P021.NH.SA.002.24 | Valid | Valid |  | 2029-12-11 | Valid | 1587/PKTN.4.8/KHP/DL/12/2019 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-11/00 | Fixed roof | SLOP OIL | Prioritas 3 | Operation | TU.594/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-06 | Valid | 2027-05-25 | P006.NH.SA.082.23 | Valid | Valid |  | 2032-11-16 | Valid | T.628/PKTN.4.5/KHP/DL/12/2022 | Good | All functional |  |  | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good With Note | - | Cleaning dan kalibrasi breather valve |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-12/00 | Floating roof | SLOP OIL | Prioritas 3 | Operation | TU.595/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-06 | Valid | 2029-01-21 | P006.NH.STH.022.25 | Valid | Valid |  | 2032-04-19 | Valid | T.309/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard | - | - | NA | NA | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-13A/00 | Floating roof | REFORMATE | Prioritas 1 | Overhaul/Cleaning | TU.596/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-06 | Valid | 2027-05-25 | P006.NH.SA.083.23 | Valid | Valid |  | 2031-12-10 | Valid | 3610/PKTN.4.8/KHP/DL/10/2021 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-13B/00 | Floating roof | REFORMATE | Prioritas 1 | Operation | TU.597/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-09 | Valid | 2029-01-21 | P006.NH.STH.023.25 | Valid | Valid |  | 2029-07-25 | Valid | 2510/PKTN.4.8/KHP/DL/07/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good With Note | Damaged but not yet causing hydrocarbon release. | Rim seal Gap & weather seal Dent/bengkok | Perbaikan menggunakan Kontrak Spot | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-15A/00 | Floating roof | LIGHT NAPHTA | Prioritas 1 | Overhaul/Cleaning | T.1667/PKTN.4.5/KN/07/2023 | 2025-07-07 | Valid | 2028-05-30 | 701/PKTN.4.8/KHP/DL/06/2017 | Valid | Valid |  | 2023-05-30 | Valid | 701/PKTN.4.8/KHP/DL/06/2017 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-15B/00 | Floating roof | LIGHT NAPHTA | Prioritas 1 | Overhaul/Cleaning | TU.598/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-07 | Valid | 2027-05-25 | P006.NH.SA.085.23 | Valid | Valid |  | 2029-10-04 | Valid | 1450/PKTN.4.8/KHP/DL/05/2019 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-17/00 | Fixed roof | SW. Stripper | Prioritas 3 | Overhaul/Cleaning | TU.599/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-09 | Valid | 2029-01-21 | P006.NH.STH.024.25 | Valid | Valid |  | 2028-07-18 | Valid | 772/PKTN.4.8/KHP/DL/08/2018 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Not Good | Non-functional | TI Existing rusak | Penggantian TI | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good With Note | Reaching the end of lifetime within less than 3 years | Temuan thinning pada shell course 5 | I/p Perbaikan shell course | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-20-18/00 | Fixed roof | FLUSHING OIL | Prioritas 3 | Operation | TU.600/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-06 | Valid | 2027-05-25 | P006.NH.SA.086.23 | Valid | Valid |  | 2033-09-06 | Valid | TU.2174/PKTN.4.5/KHP/DL/07/2023 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA | Tidak masuk daftar PM IHLA | NA | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-320-02A/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU,1348/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2025-05-25 | 014-ST/DB-MIGAS/KPB/COI/III/202 | Expired | Valid |  | 2031-10-22 | Valid | 4369/PKTN.4.8/SKHP/DL/12/2021 | Good | All functional | CLEANING OH TANK | Menunggu selesai cleaning/OH Tank | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-320-02B/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.1360/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-21 | Valid | 2025-05-25 | 014-ST/DB-MIGAS/KPB/COI/III/202 | Expired | Valid |  | 2031-08-23 | Valid | 943/PKTN.4.8/SKHP/DL/10/2021 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | D-320-12/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.1354/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-25 | Valid | 2025-01-06 | 013-ST/DB-MIGAS/KPB/COI/II/2021 | Expired | Valid |  | 2031-04-23 | Valid | 1721/PKTN.4.8/SKHP/DL/05/2021 | Good | All functional | CLEANING OH TANK | Menunggu selesai cleaning/OH Tank | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | E-01/00 | Fixed roof | BUNKER MDF | Prioritas 3 | Operation | SKHP TU.0662_PKTN.4.5_DL_02_2025 | 2027-01-27 | Valid | 2027-11-01 | 1104/48-5/TP/IP/18.01/DJM.T/2013 | Valid | Valid |  | 2034-04-01 | Valid | T.08/PKTN.4.5/KHP/DL/01/2024 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | E-02/00 | Fixed roof | BUNKER MFOLS | Prioritas 3 | Operation | TU,1359/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-20 | Valid | 2027-05-25 | P006.NH.SA.087.23 | Valid | Valid |  | 2032-02-18 | Valid | TU.888/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | E-03/00 | Fixed roof | BUNKER MFOLS | Prioritas 3 | Operation | TU.4399/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2033-06-09 | P006.NH.STH.025.25 | Valid | Valid |  | 2033-09-06 | Valid | TU.2173/PKTN.4.5/KHP/DL/07/2023 | Good | All functional | - | - | Good | Standard | - |  | Good | Standard | - | - | Good | Functional | - | - | Good | Functional | - | - | Good | Functional | - | - | Good | Functional | - | - | Good | Functional |  |  | NA | NA | - | - | NA | NA | - | - | Good | Functional | - | - | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | - | - | Tunggu Penyelesaian OH Tank | NA | NA | - | - | NA | NA | - | - | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional | - | - | Good | <25% from standard, no significant settlement | - | - | Good | Properly aligned and in good condition | - | - | Good | Operational | - | - | Good | Functional | - | - | Good | Functional | - | - | NA | NA | - | - | NA | NA | - | - | Good | Good, no significant corrosion | - | - | NA | NA | - | - | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | E-04/00 | Fixed roof | BUNKER MFOLS | Prioritas 3 | Operation | TU.4400/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.026.25 | Valid | Valid |  | 2034-04-01 | Valid | T.11/PKTN.4.5/KHP/DL/01/2024 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | E-05/00 | Fixed roof | BUNKER MFOLS | Prioritas 3 | Operation | TU.4401/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.027.25 | Valid | Valid |  | 2033-09-06 | Valid | TU.2172/PKTN.4.5/KHP/DL/07/2023 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional | Perbaikan Selesai |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | E-06/00 | Fixed roof | BUNKER MFOLS | Prioritas 3 | Operation | TU.4402/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.028.25 | Valid | Valid |  | 2032-03-15 | Valid | TU.975/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | - | - | Good | Standard | - | - | Good | Standard | - | - | Good | Functional | - | - | Good | Functional | - | - | Good | Functional | - | - | Good | Functional | - | - | Good | Functional |  |  | NA | NA | - | - | NA | NA | - | - | Good | Functional | - | - | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | - | - | Tunggu Penyelesaian Cleaning OH Tank | NA | NA | - | - | NA | NA | - | - | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional | - | - | Good | <25% from standard, no significant settlement | - | - | Good | Properly aligned and in good condition | - | - | Good | Operational | - | - | Good | Functional | - | - | Good | Functional | - | - | NA | NA | - | - | NA | NA | - | - | Good | Good, no significant corrosion | - | - | NA | NA | - | - | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | E-07/00 | Fixed roof | BUNKER MFOLS | Prioritas 3 | Operation | SKHP TU.0663_PKTN.4.5_DL_02_2025 | 2027-01-27 | Valid | 2029-01-21 | P006.NH.STH.029.25 | Valid | Valid |  | 2033-11-16 | Valid | TU.4444/PKTN.4.5/KHP/DL/12/2023 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-DW -CDU5 | N-01/00 | Fixed roof | FLUSHING OIL | Prioritas 3 | Operation | TU.4455/PKTN.4.5/SKHP/DL/12/2023 | 2025-11-30 | Valid | 2029-01-21 | P006.NH.STH.030.25 | Valid | Valid |  | 2030-11-18 | Valid | 3806/PKTN.4.8/KHP/DL/12/2020 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | N-02/00 | Fixed roof | SF-05 | Prioritas 3 | Overhaul/Cleaning | TU.3343/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-19 | Valid | 2029-01-21 | P006.NH.STH.031.25 | Valid | Valid |  | 2029-11-20 | Valid | 4280/PKTN.4.8/KHP/DL/12/2019 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | Leaking di area sambungan rivet shell course 1 dan nozzle reinforcement pad | Perbaikan temporary dengan composite/nonmetallic. Perbaikan permanen SOW overhaul. Percepatan overhaul tangki. | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-DW -CDU5 | N-03/00 | Fixed roof | SLOP | Prioritas 3 | Overhaul/Cleaning | TU.4455/PKTN.4.5/SKHP/DL/12/2023 | 2025-11-30 | Valid | 2029-01-21 | P006.NH.STH.032.25 | Valid | Valid |  | 2032-05-19 | Valid | TU.1827/PKTN.4.8/KHP/DL/05/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness | Leaking di area HAZ weld shell to annular plate. | Perbaikan temporary dengan composite/nonmetallic. Perbaikan permanen SOW overhaul. Percepatan overhaul tangki. | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | N-04/00 | Fixed roof | SF-05 | Prioritas 3 | Operation | TU.3344/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-19 | Valid | 2029-01-21 | P006.NH.STH.033.25 | Valid | Valid |  | 2030-10-26 | Valid | TU.2185/PKTN.4.8/KHP/DL/06/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-DW -CDU5 | N-06/00 | Fixed roof | SLOP | Prioritas 3 | Operation | TU.4455/PKTN.4.5/SKHP/DL/12/2023 | 2025-11-30 | Valid | 2029-01-21 | P006.NH.STH.034.25 | Valid | Valid |  | 2029-08-16 | Valid | 2939/PKTN.4.8/KHP/DL/08/2019 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-01/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.2318/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2029-01-21 | P006.NH.STH.035.25 | Valid | Valid |  | 2029-03-17 | Valid | TU.974/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | NA | NA | - | - | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional | - | - | Good | Functional | - | - | NA | NA | - | - | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional | - | - | Good | <25% from standard, no significant settlement | - | - | Good | Properly aligned and in good condition | - | - | Good | Operational | - | - | Good | Functional | - | - | Good | Functional | - | - | Good | Operational | - | - | NA | NA | - | - | Good | Good, no significant corrosion | - | - | NA | NA | - | - | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-02/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.4403/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.036.25 | Valid | Valid |  | 2034-04-19 | Valid | TU.1439/PKTN.4.8/KHP/DL/04/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-03/00 | Fixed roof | RFO | Prioritas 3 | Operation | TU.608/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-08 | Valid | 2029-01-21 | P006.NH.STH.037.25 | Valid | Valid |  | 2025-10-11 | Valid | TU.3880/PKTN.4.5/KHP/DL/11/2023 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-04/00 | Fixed roof | RFO | Prioritas 3 | Operation | TU.1356/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-26 | Valid | 2029-01-21 | P006.NH.STH.038.25 | Valid | Valid |  | 2029-02-21 | Valid | TU.886/PKTN.4.8/KHP/DL/03/2022 | Good | All functional |  |  | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-06/00 | Fixed roof | LSWR | Prioritas 3 | Overhaul/Cleaning | TU.2321/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2029-01-21 | P006.NH.STH.039.25 | Valid | Overdue > 3 tahun |  | 2025-10-11 | Valid | T.3881/PKTN.4.5/KHP/DL/11/2023 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-08/00 | Fixed roof | LSWR | Prioritas 3 | Operation | TU.1471/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-04 | Valid | 2029-01-21 | P006.NH.STH.040.25 | Valid | Valid |  | 2025-10-11 | Valid | TU.3882/PKTN.4.5/KHP/DL/11/2023 | Good | All functional |  |  | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-09/00 | Fixed roof | RFO | Prioritas 3 | Operation | TU,1358/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-27 | Valid | 2029-01-21 | P006.NH.STH.041.25 | Valid | Overdue > 3 tahun |  | 2032-02-20 | Valid | TU.887/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-10/00 | Fixed roof | SLOP | Prioritas 3 | Operation | TU,1341/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-19 | Valid | 2029-01-21 | P006.NH.STH.042.25 | Valid | Valid |  | 2028-11-26 | Valid | 3845/PKTN.4.8/KHP/DL/12/2018 | Good | All functional | MOD. TANK by KPB | Menunggu selesai Mod Tank oleh KPB | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA | - | - | NA | NA | - | - | Good | Functional | - | - | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional | - | - | NA | NA | - | - | NA | NA | - | - | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional | - | - | Good | <25% from standard, no significant settlement | - | - | Good | Properly aligned and in good condition | - | - | Good | Operational | - | - | Good | Functional | - | - | Good | Functional | - | - | Good | Operational | - | - | NA | NA | - | - | Good | Good, no significant corrosion | - | - | NA | NA | - | - | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-11/00 | Fixed roof | SLOP | Prioritas 3 | Operation | TU,1343/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-20 | Valid | 2029-01-21 | P006.NH.STH.043.25 | Valid | Valid |  | 2030-11-18 | Valid | 3608/PKTN.4.8/KHP/DL/12/2020 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-12/00 | Fixed roof | SLOP | Prioritas 3 | Operation | TU.1342/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-19 | Valid | 2029-01-21 | P006.NH.STH.044.25 | Valid | Valid |  | 2025-11-23 | Valid | TU.4449/PKTN.4.5/KHP/DL/12/2023 | Good | All functional | MOD. TANK by KPB | Menunggu selesai Mod Tank oleh KPB | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-13/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU,1346/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-21 | Valid | 2024-06-02 | 1104-02-BPC/293/E08-L11/P1/2020-63 | Expired | Valid |  | 2032-06-17 | Valid | TU.2180/PKTN.4.8/KHP/DL/06/2022 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-14/00 | Fixed roof | RFO | Prioritas 3 | Operation | TU.1355/PKTN.4.5/SKHP/DL/04/2024 | 2026-03-26 | Valid | 2029-01-21 | P006.NH.STH.045.25 | Valid | Valid |  | 2025-10-11 | Valid | TU.3883/PKTN.4.5/KHP/DL/11/2023 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | NA | NA | - | - | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional | - | - | Good | Functional | - | - | NA | NA | - | - | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional | - | - | Good | <25% from standard, no significant settlement | - | - | Good | Properly aligned and in good condition | - | - | Good | Operational | - | - | Good | Functional | - | - | Good | Functional | - | - | Good | Operational | - | - | NA | NA | - | - | Good | Good, no significant corrosion | - | - | NA | NA | - | - | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-15/00 | Fixed roof | MGO | Prioritas 3 | Operation | TU.1474/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-04 | Valid | 21/Jan/2029 | P006.NH.STH.046.25 | Valid | Valid |  | 2029-11-07 | Valid | 2509/PKTN.4.8/KHP/DL/07/2019 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-16/00 | Fixed roof | PERTADEX | Prioritas 2 | Operation | TU.1485/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-06 | Valid | 2024-06-02 | 1104-02-BPC/293/E08-L11/P1/2020-66 | Expired | Valid |  | 2031-09-16 | Valid | 3621/PKTN.4.8/KHP/DL/10/2021 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-17/00 | Fixed roof | SOLAR | Prioritas 2 | Operation | TU.1479/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-05 | Valid | 2029-01-21 | P006.NH.STH.048.25 | Valid | Valid |  | 2032-01-09 | Valid | TU.3449/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-18/00 | Fixed roof | DIESEL | Prioritas 2 | Operation | TU,1362/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-23 | Valid | 2029-01-21 | P006.NH.STH.049.25 | Valid | Valid |  | 2029-06-05 | Valid | 1782/PKTN.4.8/KHP/DL/06/2018 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-19/00 | Fixed roof | DIESEL | Prioritas 2 | Operation | TU,1347/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2029-01-21 | P006.NH.STH.050.25 | Valid | Valid |  | 2030-03-30 | Valid | TU.3447/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | CLEANING OH TANK | Menunggu selesai cleaning/OH Tank | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-20/00 | Fixed roof | SF-05 | Prioritas 3 | Operation | TU,1361/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-22 | Valid | 2029-01-21 | P006.NH.STH.051.25 | Valid | Overdue < 3 tahun |  | 2029-07-13 | Valid | 2508/PKTN.4.8/KHP/DL/07/2019 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-21/00 | Fixed roof | DECANT OIL | Prioritas 3 | Operation | TU,1350/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-23 | Valid | 2029-01-21 | P006.NH.STH.052.25 | Valid | Valid |  | 2032-10-13 | Valid | TU.3441/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-22/00 | Fixed roof | SF-05 | Prioritas 3 | Operation | TU.4455/PKTN.4.5/SKHP/DL/12/2023 | 2025-11-30 | Valid | 2029-05-30 | 1104-02-BPC/293/E08-L11/P1/2020-25 | Valid | Valid |  | 2032-11-29 | Valid | T.626/PKTN.4.5/KHP/DL/12/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-23/00 | Fixed roof | DECANT OIL | Prioritas 3 | Operation | TU,1353/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-23 | Valid | 2029-01-21 | P006.NH.STH.053.25 | Valid | Valid |  | 2031-03-15 | Valid | 1120/PKTN.4.8/KHP/DL/03/2021 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-24/00 | Fixed roof | DECANT OIL | Prioritas 3 | Operation | TU,1344/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-20 | Valid | 2029-01-21 | P006.NH.STH.054.25 | Valid | Overdue > 3 tahun |  | 2032-05-19 | Valid | TU.1828/PKTN.4.8/KHP/DL/05/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | O-25/00 | Fixed roof | DECANT OIL | Prioritas 3 | Operation | TU.4404/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.055.25 | Valid | Valid |  | 2033-09-15 | Valid | T.134/PKTN.4.5/KHP/DL/09/2023 | Good | All functional | ATG Tidak Masuk List PM | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | P-01/00 | Fixed roof | AVTUR | Prioritas 2 | Operation | TU.2310/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2027-05-25 | P006.NH.SA.088.23 | Valid | Valid |  | 2033-11-17 | Valid | TU.4447/PKTN.4.5/KHP/DL/12/2023 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | P-02/00 | Fixed roof | AVTUR | Prioritas 2 | Operation | TU.601/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-06 | Valid | 2027-05-25 | P006.NH.SA.089.23 | Valid | Valid |  | 2029-01-24 | Valid | TU.890/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | P-03/00 | Floating roof | LIGHT NAPHTA | Prioritas 1 | Overhaul/Cleaning | TU.4456/PKTN.4.5/SKHP/DL/12/2023 | 2025-11-30 | Valid | 2027-08-13 | 0642-02/BPC/1681/E08-L11/P1/2023-04 | Valid | Valid |  | 2033-01-16 | Valid | T.13/PKTN.4.8/KHP/DL/02/2023 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational | Perbaikan swivel joint oleh KPB |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional | Indikasi leak pada flexible hose/swivel/pivot joint & Rim seal Gap & weather seal Dent/bengkok Perbaikan menggunakan Kontrak Spot |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | P-04/00 | Floating roof | CRUDE | Prioritas 1 | Operation | SKHP TU.0664_PKTN.4.5_DL_02_2025 | 2027-01-27 | Valid | 2026-12-14 | 1919-02/BPC/1681/E08-L11/P1/2022-02 | Valid | Valid |  | 2032-05-20 | Valid | T.286/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | P-05/00 | Floating roof | CRUDE | Prioritas 1 | Overhaul/Cleaning | TU.602/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-06 | Valid | 2027-05-25 | P006.NH.SA.090.23 | Valid | Valid |  | 2032-02-19 | Valid | TU.1829/PKTN.4.8/KHP/DL/05/2022 | Good | All functional |  |  | Good | Standard |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  | TUNGGU PENYELESAIAN MOD TANK KPB | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | P-07/00 | Fixed roof | NAPHTA | Prioritas 1 | Operation | TU.4457/PKTN.4.5/SKHP/DL/12/2023 | 2025-11-30 | Valid | 2026-12-14 | 1919-02/BPC/1681/E08-L11/P1/2022-01 | Valid | Valid |  | 2029-01-26 | Valid | T.288/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | P-08/00 | Fixed roof | REFORMATE | Prioritas 1 | Operation | TU,1345/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-20 | Valid | 2027-05-25 | P006.NH.SA.091.23 | Valid | Valid |  | 2032-10-16 | Valid | TU.891/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | NA | NA | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | P-31/00 | Fixed roof | AVTUR | Prioritas 2 | Overhaul/Cleaning | TU.1476/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-05 | Valid | 2027-05-25 | P006.NH.SA.092.23 | Valid | Valid |  | 2023-11-13 | Valid | TU.889/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | P-32/00 | Fixed roof | AVTUR | Prioritas 2 | Operation | TU.1481/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-06 | Valid | 2027-05-25 | P006.NH.SA.093.23 | Valid | Valid |  | 2031-10-14 | Valid | TU.3443/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-01/00 | Fixed roof | SLOP OIL | Prioritas 3 | Operation | TU.1482/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-06 | Valid | 2029-01-21 | P006.NH.STH.056.25 | Valid | Valid |  | 2032-05-22 | Valid | 3502/PKTN.4.8/KHP/DL/12/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-02/00 | Fixed roof | SOLAR | Prioritas 2 | Overhaul/Cleaning | 1136/PKTN.4.8/KHP/DL/03/2021 | 2023-03-27 | Expired | 2027-12-20 | 137/48-5/TP/IP/18.01/DJM.T/2018 | Valid | Valid |  | 2030-01-25 | Valid | 070/PKTN.4.8/KHP/DL/01/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-03/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.2269/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-12 | Valid | 2029-01-21 | P006.NH.STH.057.25 | Valid | Valid |  | 2021-11-18 | Valid | TU.2033/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-04/00 | Fixed roof | SOLAR | Prioritas 2 | Overhaul/Cleaning | TU.3525/PKTN.4.5/SKHP/DL/11/2022 | 2024-10-24 | Expired | 2027-05-25 | P006.NH.SA.097.23 | Valid | Valid |  | 2031-10-26 | Valid | 3622/PKTN.4.8/KHP/DL/10/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Not Good | Damage causing hydrocarbon release; reaching retiring thickness |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-05/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.3348/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-20 | Valid | 2029-01-21 | P006.NH.STH.058.25 | Expired | Overdue > 3 tahun |  | 2032-03-16 | Valid | TU.2036/PKTN.4.8/KHP/DL/06/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-06/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.3353/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-21 | Valid | 2029-01-21 | P006.NH.STH.059.25 | Valid | Valid |  | 2032-04-18 | Valid | TU.1830/PKTN.4.8/KHP/DL/05/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good |  |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-07/00 | Fixed roof | SOLAR | Prioritas 2 | Overhaul/Cleaning | TU.3349/PKTN.4.5/SKHP/DL/10/2023 | 2025-09-20 | Valid | 2029-01-21 | P006.NH.STH.060.25 | Valid | Valid |  | 2032-05-20 | Valid | 504/PKTN.4.8/KHP/DL/02/2020 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-08/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.0666_PKTN.4.5_DL_02_2025 | 2027-01-27 | Valid | 2027-05-25 | P006.NH.SA.101.23 | Valid | Valid |  | 2029-02-25 | Valid | T.451/PKTN.4.8/KHP/DL/06/2022 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | NA | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-09/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.607/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-06 | Valid | 2027-05-25 | P006.NH.SA.102.23 | Valid | Valid |  | 2029-09-16 | Valid | 204/SPK.5.8.16/S/DL/01/2016 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-10/00 | Fixed roof | SLOP OIL | Prioritas 3 | Operation | TU.0667_PKTN.4.5_DL_02_2025 | 2027-01-27 | Valid | 2029-01-21 | P006.NH.STH.061.25 | Valid | Valid |  | 2032-11-14 | Valid | TU.2183/PKTN.4.8/KHP/DL/06/2022 | Good | All functional | ATG Rusak | I/p material tiba (PO: 4500067341) | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional | - | - | Good | Functional | - | - | Good | Functional | - | - | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional | - | - | Good | Functional | - | - | NA | NA | - | - | Good | Good | - | - | Good | Lifetimhhhhte ≥ 3 years, no damage | - | - | Good | Lifetime ≥ 3 years, no damage | - | - | Good | Functional | - | - | Good | <25% from standard, no significant settlement | - | - | Good | Properly aligned and in good condition | - | - | Good | Operational | - | - | Good | Functional | - | - | Good | Functional | - | - | Good | Operational | - | - | NA | NA | - | - | Good | Good, no significant corrosion | - | - | NA | NA | - | - | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | R-11/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | SKHP TU.0668_PKTN.4.5_DL_02_2025 | 2027-01-27 | Valid | 2027-05-25 | P006.NH.SA.104.23 | Valid | Valid |  | 2032-05-23 | Valid | TU.3446/PKTN.4.8/KHP/DL/10/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-DW -DHP | T-01A/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2029-01-21 | P006.NH.STH.062.25 | Valid | Valid |  | 2025-09-16 | Valid | TU.976/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard |  | - | Good | Standard |  | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-DW -DHP | T-01B/00 | Fixed roof | Slop Oil | Prioritas 3 | Operation | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2029-01-21 | P006.NH.STH.063.25 | Valid | Valid |  | 2025-09-16 | Valid | TU.2182/PKTN.4.8/KHP/DL/06/2022 | Good | All functional | NA | NA | Good | Standard |  | - | Good | Standard |  | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | T-201/00 | Fixed roof | LAWS-05 | Prioritas 3 | Overhaul/Cleaning | TU.609/PKTN.4.5/SKHP/DL/04/2024 | 2026-02-08 | Valid | 2029-01-21 | P006.NH.STH.064.25 | Valid | Valid |  | 2030-11-18 | Valid | T.12/PKTN.4.5/KHP/DL/01/2024 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | T-202/00 | Fixed roof | LAWS-05 | Prioritas 3 | Operation | TU.603/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-07 | Valid | 2029-01-21 | P006.NH.STH.065.25 | Valid | Valid |  | 2032-10-15 | Valid | TU.1826/PKTN.4.8/KHP/DL/05/2022 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | T-203/00 | Fixed roof | LAWS-05 | Prioritas 3 | Overhaul/Cleaning | TU.604/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-07 | Valid | 2029-01-21 | P006.NH.STH.066.25 | Valid | Valid |  | 2032-10-14 | Valid | TU.2035/PKTN.4.8/KHP/DL/06/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | T-900/00 | Fixed roof | PERTALITE | Prioritas 1 | Overhaul/Cleaning | TU.930/PKTN.4.5/SKHP/DL/03/2023 | 2025-03-15 | Expired | 2022-12-20 | 150/48-5/TP/IP/18.01/DJM.T/2018 | Expired | Valid |  | 2030-11-18 | Expired | 068/PKTN.4.8/KHP/DL/01/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | T-901/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.4405/PKTN.4.5/DL/10/2024 | 2026-09-27 | Valid | 2029-01-21 | P006.NH.STH.067.25 | Valid | Valid |  | 2032-03-14 | Valid | 1489/SPK.5.8/DL/04/2016 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | T-902/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Overhaul/Cleaning | TU,1349/PKTN,4,5/SKHP/DL/04/2024 | 2026-03-23 | Valid | 2027-05-25 | P006.NH.SA.106.23 | Valid | Valid |  | 2028-11-27 | Valid | TU.4251/PKTN.4.5/KHP/DL/12/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | T-903/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | SKHP TU.0669_PKTN.4.5_DL_02_2025 | 2027-01-27 | Valid | 2027-05-25 | P006.NH.SA.107.23 | Valid | Valid |  | 2030-11-26 | Valid | TU.4252/PKTN.4.5/KHP/DL/12/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | T-904/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | SKHP TU.0670_PKTN.4.5_DL_02_2025 | 2027-01-27 | Valid | 2024-06-12 | 1104-02-BPC/293/E08-L11/P1/2020-34 | Expired | Valid |  | 2030-11-17 | Valid | TU.1825/PKTN.4.8/KHP/DL/05/2022 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-UTL -STEAM | U-10/00 | Fixed roof | RFO | Prioritas 3 | Operation | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2029-01-21 | P006.NH.STH.069.25 | Valid | Valid |  | 2029-08-18 | Valid | TU.3206/PKTN.4.5/KHP/DL/09/2023 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-UTL -STEAM | U-11/00 | Fixed roof | RFO | Prioritas 3 | Operation | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2029-01-21 | P006.NH.STH.070.25 | Valid | Valid |  | 2028-07-21 | Valid | 3612/PKTN.4.5/KHP/DL/09/2023 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-UTL -STEAM | U-12/00 | Fixed roof | RFO | Prioritas 3 | Operation | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2029-01-21 | P006.NH.STH.071.25 | Valid | Valid |  | 2029-11-21 | Valid | 3505/PKTN.4.8/KHP/DL/12/2020 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-UTL -STEAM | U-13/00 | Fixed roof | RFO | Prioritas 3 | Operation | TU.4455/PKTN.4.5/SKHP/DL/12/2023 | 2025-11-30 | Valid | 2029-01-21 | P006.NH.STH.072.25 | Valid | Valid |  | 2025-09-06 | Valid | TU.2171/PKTN.4.5/KHP/DL/07/2023 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-UTL -STEAM | U-14/00 | Fixed roof | RFO | Prioritas 3 | Operation | TU.2273/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2023-10-10 | 4137/BOEAAM | Expired | Valid |  | 2029-08-11 | Valid | 1597/PKTN.4.8/KHP/DL/12/2019 | Good | All functional | NA | NA | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | V-01/00 | Fixed roof | SLOP | Prioritas 3 | Operation | TU.2314/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2029-01-21 | P006.NH.STH.074.25 | Valid | Valid |  | 2032-10-15 | Valid | T.557/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | V-02/00 | Fixed roof | SLOP | Prioritas 3 | Operation | TU.2315/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2029-01-21 | P006.NH.STH.075.25 | Valid | Valid |  | 2032-10-14 | Valid | T.556/PKTN.4.8/KHP/DL/10/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | V-03/00 | Fixed roof | SLOP | Prioritas 3 | Operation | SKHP TU.0671_PKTN.4.5_DL_02_2025 | 2027-01-27 | Valid | 2029-01-21 | AP006.NH.STH.076.25 | Valid | Valid |  | 2034-05-01 | Valid | T.10/PKTN.4.5/KHP/DL/01/2024 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | V-04/00 | Fixed roof | SLOP | Prioritas 3 | Operation | TU.605/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-09 | Valid | 2029-01-21 | P006.NH.STH.077.25 | Valid | Valid |  | 2034-05-01 | Valid | T.09/PKTN.4.5/KHP/DL/01/2024 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | V-05/00 | Fixed roof | SLOP | Prioritas 3 | Operation | TU.606/PKTN.4.5/SKHP/DL/02/2024 | 2026-02-07 | Valid | 2029-01-21 | P006.NH.STH.078.25 | Valid | Valid |  | 2030-11-18 | Valid | 3609/PKTN.4.8/KHP/DL/12/2020 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | V-06/00 | Fixed roof | SLOP | Prioritas 3 | Operation | TU.2316/PKTN.4.5/DL/03/2025 | 2027-03-08 | Valid | 2029-01-21 | P006.NH.STH.079.25 | Valid | Valid |  | 2032-03-14 | Valid | TU.977/PKTN.4.8/KHP/DL/03/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-TBL -BPP | V-07/00 | Fixed roof | SLOP | Prioritas 3 | Overhaul/Cleaning | TU.1477/PKTN.4.5/SKHP/DL/05/2023 | 2025-05-05 | Valid | 2029-01-21 | P006.NH.STH.080.25 | Valid | Valid |  | 2028-11-27 | Valid | 3872/PKTN.4.8/KHP/DL/12/2018 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA | TIDAK TERPASANG FGDS | NA | Good | Functional | NA | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-DW -HVU3 | V-10/00 | Fixed roof | SLOP OIL | Prioritas 3 | Operation | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2029-01-21 | P006.NH.STH.081.25 | Valid | Valid |  | 2030-11-26 | Valid | TU.2184/PKTN.4.8/KHP/DL/06/2022 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-DW -HVU3 | V-11/00 | Fixed roof | SLOP OIL | Prioritas 3 | Overhaul/Cleaning | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2029-01-21 | P006.NH.STH.082.25 | Valid | Valid |  | 2030-11-17 | Valid | 3504/PKTN.4.8/KHP/DL/12/2020 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-DW -DHP | V-16/00 | Fixed roof | SLOP OIL | Prioritas 3 | Operation | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2029-01-21 | P006.NH.STH.083.25 | Valid | Valid |  | 2029-08-18 | Valid | 3909/PKTN.4.8/KHP/DL/11/2019 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-DW -DHP | V-17/00 | Fixed roof | SLOP OIL | Prioritas 3 | Operation | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2029-01-21 | P006.NH.STH.084.25 | Valid | Valid |  | 2028-07-21 | Valid | 773/PKTN.4.8/KHP/DL/08/2018 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU V Balikpapan | RU05-TBL | RU05-DW -DHP | V-17B/00 | Fixed roof | SLOP OIL | Prioritas 3 | Operation | TU.2274/PKTN.4.5/SKHP/DL/07/2023 | 2025-07-14 | Valid | 2029-01-21 | P006.NH.STH.085.25 | Valid | Valid |  | 2029-11-21 | Valid | 4281/PKTN.4.8/KHP/DL/12/2019 | Good | All functional | NA | NA | Good | Standard | - | - | Good | Standard | - | - | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | Good | Functional |  | NA | NA | NA | Tidak masuk daftar PM IHLA | NA | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | TIDAK TERPASANG & MASUK COVERED LPS | NA | NA | NA | TIDAK ADA CATHODIC | NA | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | NA | NA |  |  | 2026-07-28
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-101A/00 | Floating roof | CRUDE OIL | Prioritas 1 | Operation | TU.3836/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4139-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2032-04-04 | Valid | TU.1309/PKTN.4.8/KHP/DL/04/2022 | Good | All functional |  |  | Good | Standard | Penggantian TSI tgl 29.8.2022 |  | Good | Standard | Penggantian TSI tgl 29.8.2022 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V | setting trafo perlu dinaikan |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-101B/00 | Floating roof | CRUDE OIL | Prioritas 1 | Operation | TU.3815/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4140-02-ENI/180/E03-L11/PI/2021 | Expired | Overdue > 3 tahun |  | 2027-11-30 | Valid | TU.0873/PKTN.4.5/DL/01/2026 | Good | All functional |  |  | Good | Standard | Penggantian ATG baru tgl 30-09-2022 |  | Good | Standard | Penggantian ATG baru tgl 30-09-2022 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-101C/00 | Floating roof | CRUDE OIL | Prioritas 1 | Operation | TU.3816/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4141-02-ENI/180/E03-L11/PI/2021 | Expired | Overdue > 3 tahun |  | 2027-07-19 | Valid | TU.6732/PKTN.4.5/DL/08/2025 | Good | All functional |  |  | Good | Standard | Penggantian ATG baru tgl 28-09-2022 |  | Good | Standard | Penggantian ATG baru tgl 28-09-2022 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-101D/00 | Floating roof | CRUDE OIL | Prioritas 1 | Operation | TU.3817/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2029-09-08 | P013.NH.ASG.001.26 | Valid | Valid |  | 2031-10-04 | Valid | T.11883/PKTN.4.5/DL/11/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-101E/00 | Floating roof | CRUDE OIL | Prioritas 1 | Operation | TU.3818/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4142-02-ENI/180/E03-L11/P1/2021 | Expired | Overdue > 3 tahun |  | 2027-11-30 | Valid | TU.0874/PKTN.4.5/DL/01/2026 | Good | All functional |  |  | Good | Standard | Penggantian TSI tgl 29.8.2022 |  | Good | Standard | Penggantian TSI tgl 29.8.2022 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-101F/00 | Floating roof | CRUDE OIL | Prioritas 1 | Operation | TU.3819/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4143-02-ENI/180/E03-L11/P1/2021 | Expired | Overdue > 3 tahun |  | 2027-07-19 | Valid | TU.6723/PKTN.4.5/DL/08/2025 | Good | All functional |  |  | Good | Standard | Penggantian ATG baru tgl 30-09-2022 |  | Good | Standard | Penggantian ATG baru tgl 30-09-2022 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-101G/00 | Floating roof | CRUDE OIL | Prioritas 1 | Operation | TU.3820/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4144-02-ENI/180/E03-L11//PI/2021 | Expired | Overdue > 3 tahun |  | 2027-11-30 | Valid | TU.0875/PKTN.4.5/DL/01/2026 | Good | All functional |  |  | Good | Standard | Penggantian ATG baru tgl 28-09-2022 |  | Good | Standard | Penggantian ATG baru tgl 28-09-2022 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-102A/00 | Floating roof | MINAS CRUDE | Prioritas 1 | Operation | TU.3821/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4145-02-ENI/180/E03-L11/PI/2021 | Expired | Overdue > 3 tahun |  | 2027-07-19 | Valid | TU.4653/PKTN.4.5/KHP/DL/12/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | kebocoran shell ditemukan 2 titik rembesan crude oil pada FRP wrapping | Temporary di Lakukan rerating dengan penurunan high level liquid menjadi 9000 mm, jangka panjang : perbaikan shell course / Overhaul | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional | Korosi |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-102B/00 | Floating roof | MINAS CRUDE | Prioritas 1 | Operation | TU.14907/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2029-09-08 | P013.NH.ASG.216.25 | Valid | Valid |  | 2031-07-17 | Valid | TU.6722/PKTN.4.5/DL/08/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-103A/00 | Fixed roof | AVTUR | Prioritas 3 | Operation | TU.14908/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2025-12-16 | 4147-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2034-01-09 | Valid | T.20/PKTN.4.5./KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Roof plate terkorosi dan bergelombang | Direkomendasikan untuk dilakukan penggantian total roof pada saat overhaul agustus 2026 | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-103B/00 | Fixed roof | GO HTU FEED | Prioritas 3 | Overhaul/Cleaning | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-16 | 4148-02-ENI/180/E03-L11/PI/2021 | Expired | Valid |  | 2028-09-30 | Valid | 3065/PKTN.4.8/KHP/DL/10/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Deck plate bergelombang dan korosi | Total penggantian roof pada kesempatan pertama | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-104A/00 | Fixed roof | ARHDM FEED | Prioritas 3 | Overhaul/Cleaning | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-16 | 4149-02-ENI/180/E03-L11/P1/2021 | Expired | Overdue > 3 tahun |  | 2027-07-19 | Valid | TU.6727/PKTN.4.5/DL/08/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Pitting pada shell course 1 | telah dilakukan derating dari lvl 13980mm ke 12300mm dan akan dilakukan insert plate pada saat OH | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-104B/00 | Fixed roof | ARHDM FEED | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2029-01-24 | P013.N.H.ASG.086.25 | Valid | Valid |  | 2031-03-20 | Valid | /PKTN.4.5/SKHP/DL/04/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good With Note | Non-functional | FCU MOV error | perbaikan mov | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-105A/00 | Fixed roof | RCC FEED | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-16 | 4151-02-ENI/180/E03-L11/P1/2021 | Expired | Overdue > 3 tahun |  | 2027-07-19 | Valid | TU.6728/PKTN.4.5/DL/08/2025 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Pitting pada shell course 1 | telah dilakukan derating level dari 13860mm ke 11200mm dan disarankan untuk recoating, jangka panjang : perbaikan shell course / Overhaul | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-105B/00 | Fixed roof | RCC FEED | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-31 | 10203-02-ENI/146/E08-L11/PI/2022 | Expired | Valid |  | 2032-01-14 | Valid | T.280/PKTN.4.8/KHP/DL/01/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | motor dan mixer tidak terkoneksi |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-106/00 | Fixed roof | AVTUR | Prioritas 3 | Operation | TU.14909/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2030-04-14 | P013.NH.EW.027.26 | Valid | Valid |  | 2034-01-09 | Valid | TU. 451/PKTN.4.5./KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-107A/00 | Floating roof | Naphtha Intermedia | Prioritas 3 | Operation | TU.14910/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2028-10-01 | MIT-2024.2065-14724-ST | Valid | Valid |  | 2029-02-28 | Valid | 260/PKTN.4.8/KHP/DL/03/2019 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-107B/00 | Floating roof | Naphtha Intermedia | Prioritas 3 | Operation | TU.14911/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2030-07-15 | P013.NH.EW.242.26 | Valid | Valid |  | 2032-03-07 | Valid | T.2196/PKTN.4.5/DL/03/2026 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-107C/00 | Floating roof | Naphtha Intermedia | Prioritas 3 | Operation | TU.3821/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4154-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2033-11-01 | Valid | TU.4645/PKTN.4.5/KHP/DL/12/2023 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | thinning pada shell course 2,3,5 | full recoating shell sesuai memo no 1001/KPI49142/2023-S5 dan derating dari level 13900mm ke 10000mm, jangka panjang : perbaikan shell course / Overhaul | Good With Note | Reaching the end of lifetime within less than 3 years | Kebocoran roof deck plate 42-T-107C (repetitive case) : 1. Bocoran sebelumnya (repetitive) di orientasi 220 deg 2. bocoran pada roof plate pada orientasi 225 deg 3. bocoran pada roof plate pada orientasi 270 deg | Permanent repair : Penggantian total roof pada overhaul januari 2027 | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-107D/00 | Floating roof | Naphtha Intermedia | Prioritas 3 | Operation | TU.14912/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2028-10-01 | MIT-2024.2065-14725-ST | Valid | Overdue > 3 tahun |  | 2032-04-08 | Valid | TU.2618/PTKN.4.8/KHP/DL/08/2022 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-201A/00 | Floating roof | SR/HDM NAPHTA | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-25 | 4155-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2028-07-31 | Valid | 2242/PKTN.4.8/KHP/DL/07/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional | motor dan mixer tidak terkoneksi | koneksikan kembali motor dengan mixer | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-201B/00 | Floating roof | SR/HDM NAPHTA | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-16 | 4156-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2028-07-31 | Valid | 2240/PKTN.4.8/KHP/DL/07/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-202A/00 | Floating roof | POLY GASOLINE | Prioritas 1 | Operation | TU.14913/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2028-06-27 | P013.NH.SA.097.24 | Valid | Valid |  | 2028-06-27 | Valid | 2241/PKTN.4.8/KHP/DL/07/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | Proses overhaul |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V | Proses overhaul |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-202B/00 | Floating roof | POLY GASOLINE | Prioritas 1 | Operation | TU.3814/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2026-09-01 | 12099-02-ENI/134/E08-L11/PI/2022 | Valid | Valid |  | 2028-07-31 | Valid | 2243/PKTN.4.8/KHP/DL/07/2018 | Good | All functional |  |  | Good | Standard | Penggantian ATG baru tgl 29-09-2022 |  | Good | Standard | Penggantian ATG baru tgl 29-09-2022 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-203A/00 | Fixed roof | INTERMEDIATE PRODUCT | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-16 | 4159-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2031-01-11 | Valid | 4052/PKTN.4.8/SKHP/DL/11/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | thinning pada shell course 2 & 3 | telah dilakukan derating level dari 13390mm ke 12250mm dan disarankan untuk recoating, jangka panjang : perbaikan shell course / Overhaul | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-203B/00 | Fixed roof | INTERMEDIATE PRODUCT | Prioritas 3 | Operation | TU.14914/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2028-07-05 | P013.NH.EW.099.24 | Valid | Valid |  | 2028-07-31 | Valid | 2647/PKTN.4.8/DL/08/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-204/00 | Fixed roof | INTERMEDIATE PRODUCT | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-16 | 4161-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2028-07-31 | Valid | 2648/PKTN.4.8/KHP/DL/08/018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-205A/00 | Floating roof | HOMC | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-16 | 4162-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2028-09-30 | Valid | 3068/PKTN.4.8/KHP/DL/10/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | motor dan mixer tidak terkoneksi | koneksikan kembali motor dengan mixer | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good With Note | Some non-functional but not leaking | deck drainage bocor | pengecekan terlebih dahulu posisi kebocoran | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-205B/00 | Floating roof | HOMC | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-16 | 4163-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2028-09-30 | Valid | 3067/PKTN.4.8/KHP/DL/10/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-206/00 | Fixed roof | DECANT OIL | Prioritas 2 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2028-07-05 | P013.NH.EW.098.24 | Valid | Valid |  | 2028-07-05 | Valid | 3551/PKTN.4.8/KHP/DL/10/2021 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-301A/00 | Floating roof | GASOLINE | Prioritas 1 | Operation | TU.3834/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2026-03-15 | 4858-02-ENI/66/E08-L11/P1/2022 | Expired | Valid |  | 2032-04-27 | Valid | T.1748/PKTN.4.8/KHP/DL/05/2022 | Good | All functional |  |  | Good | Standard | Normal Operasi |  | Good | Standard | Normal Operasi |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional | motor dan mixer tidak terkoneksi | koneksikan kembali motor dengan mixer | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-301B/00 | Floating roof | HOMC | Prioritas 1 | Operation | TU.14915/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2025-12-16 | 4165-02-ENI/180/E03-L11/PI/2021 | Expired | Valid |  | 2032-04-08 | Valid | TU.2620/PTKN4.8/KHP/DL/08/2022 | Good | All functional |  |  | Good | Standard | Penggantian unit baru ATG type FW9411NNE tgl 19-08-2022 |  | Good | Standard | Penggantian unit baru ATG type FW9411NNE tgl 19-08-2022 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | thinning pada shell course 2 | telah dilakukan derating level dari 13900mm ke 11500mm dan disarankan untuk recoating, jangka panjang : perbaikan shell course / Overhaul | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | NA | NA | Secara P&ID tidak dilengkapi PSV |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-301C/00 | Floating roof | Naphtha Intermedia | Prioritas 1 | Overhaul/Cleaning | TU.14916/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2025-12-16 | 4166-02-ENI/180/E03-L11/PI/2021 | Expired | Overdue > 3 tahun |  | 2033-11-01 | Valid | TU.4646/PKTN.4.5/KHP/DL/12/2023 | Good | All functional |  |  | Good | Standard | Telah dilakukan verifikasi level ATG tgl 16/01/23 |  | Good | Standard | Telah dilakukan verifikasi level ATG tgl 16/01/23 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | deformasi pada shell course 4 | Temporary di Lakukan rerating dengan penurunan high level liquid menjadi 11800 mm, jangka panjang : perbaikan shell course / Overhaul | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-301D/00 | Floating roof | HOMC | Prioritas 1 | Operation | TU.3823/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4167-02-ENI/180/E03-L11/PI/2021 | Expired | Valid |  | 2033-11-01 | Valid | TU.4647/PKTN.4.5/KHP/DL/12/2023 | Good | All functional |  |  | Good | Standard | Penggantian unit baru ATG type FW9411NNE tgl 23-09-22 |  | Good | Standard | Penggantian unit baru ATG type FW9411NNE tgl 23-09-22 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Thinning pada shell course 2 | Derating dari level 13900mm ke 12100mm, reff memo no. 1410/KPI49142/2022-S5, jangka panjang : perbaikan shell course / Overhaul | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-301E/00 | Floating roof | GASOLINE | Prioritas 1 | Operation | T.3136/PKTN.4.5/DL/04/2025 | 2027-04-25 | Valid | 2029-06-10 | 224/JB562/TP-FT/01/VI/2025 | Valid | Valid |  | Mei 2031 | Valid | DL-T-25-1272-001 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-301F/00 | Floating roof | GASOLINE | Prioritas 1 | Operation | T.3138/PKTN.4.5/DL/04/2025 | 2027-04-25 | Valid | 2029-06-10 | 225/JB562/TP-FT/02/VI/2025 | Valid | Valid |  | Juni 2031 | Valid | DL-T-25-1276-001 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-301G/00 | Floating roof | GASOLINE | Prioritas 1 | Operation | T.3137/PKTN.4.5/DL/04/2025 | 2027-04-25 | Valid | 2029-06-10 | 226/JB562/TP-FT/03/VI/2025 | Valid | Valid |  | Juni 2031 | Valid | DL-T-25-1276-002 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-301H/00 | Floating roof | GASOLINE | Prioritas 1 | Operation | T.3139/PKTN.4.5/DL/04/2025 | 2027-04-25 | Valid | 2029-06-10 | 227/JB562/TP-FT/01/VI/2025 | Valid | Valid |  | Juni 2031 | Valid | DL-T-25-1276-003 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-302A/00 | Floating roof | Kerosene Tank | Prioritas 2 | Operation | TU.3824/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4168-02-ENI/180/E03-L11/PI/2021 | Expired | Valid |  | 2034-01-10 | Valid | TU. 449/PKTN.4.5./KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard | Penggantian unit baru ATG type FW94111NNE tgl 24-08-22 |  | Good | Standard | Penggantian unit baru ATG type FW94111NNE tgl 24-08-22 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V | setting trafo perlu dinaikan |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-302B/00 | Floating roof | Kerosene Tank | Prioritas 2 | Operation | TU.14917/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2025-12-16 | 4169-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2034-01-11 | Valid | TU. 450/PKTN.4.5./KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard | Normal Operasi |  | Good | Standard | Normal Operasi |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V | setting trafo perlu dinaikan |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Operational |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-303A/00 | Fixed roof | ADO/IDF | Prioritas 2 | Operation | TU.14918/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2025-12-16 | 4170-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2034-01-16 | Valid | TU. 452/PKTN.4.5./KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard | Penggantian unit baru ATG type FW94111NNE tgl 24-08-22 |  | Good | Standard | Penggantian unit baru ATG type FW94111NNE tgl 24-08-22 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V | setting trafo perlu dinaikan |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Temuan roof berlubang dekat area lubang sample/sounding | Sudah dilakukan temporary wraping. Perlu dilakukan perbaikan total roof | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  | lakukan penggantian tie rod dengan size existing | Good With Note | Misaligned | tie rod EBJ rusakk 1 pada line inlet dan lepas 3 pada line outlet | lakukan penggantian tie rod dengan size existing | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-303B/00 | Fixed roof | ADO/IDF | Prioritas 2 | Operation | TU.14919/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2028-10-01 | MIT-2024.2065-14726-ST | Valid | Valid |  | 2034-01-14 | Valid | TU. 453/PKTN.4.5./KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard | tgl 16-6-2023 dilakukan subtitusi ATG dari tanki 42-T-202A dikarenakan sertifikat ATG overdue |  | Good | Standard | tgl 16-6-2023 dilakukan subtitusi ATG dari tanki 42-T-202A dikarenakan sertifikat ATG overdue |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | Good | Functional |  |  | Good | Within the range of -0.85 to -1.5 V | setting trafo perlu dinaikan |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-304A/00 | Fixed roof | IDO/IDF | Prioritas 2 | Overhaul/Cleaning | TU.3825/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4171-02-ENI/180/E03-L11/PI/2021 | Expired | Valid |  | 2028-01-09 | Valid | 3066/PKTN.4.8/KHP/DL/10/2018 | Good | All functional |  |  | Good | Standard | Penggantian ATG baru tgl 03/10/2022 |  | Good | Standard | Penggantian ATG baru tgl 03/10/2022 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | deck plate roof secara keseluruhan terkorosi parah dan sudah dilakukan >50% wrapping | lakukan penggantian total roof plate dan lakukan pemeriksaan secara berkala | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-304B/00 | Fixed roof | IDO/IDF | Prioritas 2 | Operation | TU.14920/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2025-12-16 | 4172-02-ENI/180/E03-L11/PI/2021 | Expired | Valid |  | 2028-07-31 | Valid | 657/PKTN.4.8/KHP/DL/07/2018 | Good | All functional |  |  | Good | Standard | telah dilakukan verifikasi level ATG tgl 04/01/2023 |  | Good | Standard | telah dilakukan verifikasi level ATG tgl 04/01/2023 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-304C/00 | Fixed roof | IDO/IDF | Prioritas 2 | Operation | TU.14921/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2025-12-16 | 4188-02-ENI/180/E03-L11/PI/2021 | Expired | Valid |  | 2034-01-19 | Valid | TU. 454/PKTN.4.5./KHP/DL/02/2024 | Good | All functional |  |  | Good | Standard | Normal Operasi |  | Good | Standard | Normal Operasi |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-305A/00 | Fixed roof | DCO/FO | Prioritas 2 | Operation | TU.3826/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2025-12-16 | 4173-02-ENI/180/E03-L11/PI/2021 | Expired | Overdue > 3 tahun |  | 2027-07-19 | Valid | TU.6725/PKTN.4.5/DL/08/2025 | Good | All functional |  |  | Good | Standard | ATG berfungsi normal, perlu penggantian elemen ATS nomor 4 rusak |  | Good | Standard | ATG berfungsi normal, perlu penggantian elemen ATS nomor 4 rusak |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Pitting pada Shell course 1 | Telah dilakukan derating level dari 13980mm ke 12100mm dan jangka panjang akan dilakukan penggantian shell pada saat OH | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-305B/00 | Fixed roof | DCO/FO | Prioritas 2 | Operation | TU.14922/PKTN.4.5/DL/12/2025 | 30 Nov 2027 | Valid | 2025-12-16 | 4174-02-ENI/180/E03-L11/PI/2021 | Expired | Overdue > 3 tahun |  | 2027-07-19 | Valid | TU.6726/PKTN.4.5/DL/08/2025 | Good | All functional |  |  | Good | Standard | Penggantian unit baru ATG type FW94111NNE tgl 25-08-22 |  | Good | Standard | Penggantian unit baru ATG type FW94111NNE tgl 25-08-22 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Pitting pada Shell course 1 | Telah dilakukan derating level dari 13980mm ke 10000mm dan jangka panjang akan dilakukan penggantian shell pada saat OH | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-401A/00 | Spherical Tank | PROPANE | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-02-08 | 4046-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2028-12-31 | Valid | 1496/PKTN.4.7/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-401B/00 | Spherical Tank | PROPANE | Prioritas 3 | Overhaul/Cleaning | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-02-08 | 4047-02-ENI/62/E03-L11/P1/2022 | Valid | Overdue < 3 tahun |  | 2029-07-31 | Valid | 2758/PKTN.4.8/KHP/DL/08/2017 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-402A/00 | Spherical Tank | BUTHANE | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-02-08 | 4048-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2028-12-31 | Valid | 1493/PKTN.4.7/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-402B/00 | Spherical Tank | BUTHANE | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-02-08 | 4049-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2029-07-31 | Valid | 2759/PKTN.4.8/KHP/DL/08/2017 | Good | All functional |  |  | Good | Standard | Salah satu Bonding tertutup tanah | penggalian tanah | Good | Standard | Salah satu Bonding tertutup tanah | penggalian tanah | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-403A/00 | Spherical Tank | LPG MIX | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-02-08 | 4050-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2029-07-31 | Valid | 2760/PKTN.4.8/KHP/DL/08/2017 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-403B/00 | Spherical Tank | LPG MIX | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-02-08 | 4051-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2028-12-31 | Valid | 1494/PKTN.4.7/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-403C/00 | Spherical Tank | LPG MIX | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-06-26 | 4355-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2029-08-31 | Valid | 2761/PKTN.4.8/KHP/DL/08/2017 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-403D/00 | Spherical Tank | LPG MIX | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-06-26 | 4356-02-ENI/62/E03-L11/P1/2022 | Valid | Overdue < 3 tahun |  | 2029-08-31 | Valid | 2762/PKTN.4.8/KHP/DL/08/2017 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-404A/00 | Spherical Tank | PROPYLENE | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-02-08 | 4054-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2028-12-31 | Valid | 1495/PKTN.4.7/12/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-404B/00 | Spherical Tank | PROPYLENE | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-02-08 | 4055-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2029-08-31 | Valid | 2763/PKTN.4.8/KHP/DL/08/2017 | Good | All functional |  |  | Good | Standard | ATG dalam kondisi baik. Telah dilakukan penggantian |  | Good | Standard | ATG dalam kondisi baik. Telah dilakukan penggantian |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-404C/00 | Spherical Tank | PROPYLENE | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-06-26 | 4357-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2030-10-31 | Valid | 1232/PKTN.4.7/KHP/11/2018 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-404D/00 | Spherical Tank | PROPYLENE | Prioritas 3 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2027-06-26 | 4358-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2029-08-31 | Valid | 2764/PKTN.4.8/KHP/DL/08/2017 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-404E/00 | Spherical Tank | PROPYLENE | Prioritas 3 | Operation | TU.3827/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2026-06-30 | 3467-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2028-04-30 | Valid | 2711/SPK.5.8/KHP/DL/06/2016 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-404F/00 | Spherical Tank | PROPYLENE | Prioritas 3 | Operation | TU.3839/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2026-06-30 | 3468-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2028-04-30 | Valid | 2712/SPK.5.8/KHP/DL/06/2016 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, terdapat temuan hasil NDT pada internal shell |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-404G/00 | Spherical Tank | PROPYLENE | Prioritas 3 | Operation | TU.3829/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2026-06-30 | 3469-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2028-04-30 | Valid | 2713/SPK.5.8/KHP/DL/06/2016 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-404H/00 | Spherical Tank | PROPYLENE | Prioritas 3 | Idle | TU.3832/PTKN.4.5/DL/09/2024 | 8 Sept 2026 | Valid | 2026-06-30 | 3470-02-ENI/62/E03-L11/P1/2022 | Valid | Valid |  | 2028-04-30 | Valid | 2714/SPK.5.8/KHP/DL/06/2016 | Good | All functional |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | Pemasangan LPS tahap 4 |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good With Note | Reaching the end of lifetime within less than 3 years | Terdapat 3 titik crack baru setelah repair | Perbaikan 3 crack | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | NA | NA |  |  | NA | NA |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | NA | NA |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Cracked at support columns over ≤50% |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-503/00 | Fixed roof | B/O FLUSH | Prioritas 2 | Overhaul/Cleaning | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2026-09-16 | 12100-02-ENI/134/E08-L11/PI/2022 | Valid | Valid |  | 2032-01-11 | Valid | TU.3830/PKTN.4.8/DL/11/2022 | Good | All functional |  |  | Good | Standard | Normal Operasi |  | Good | Standard | Normal Operasi |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -TBM | 42-T-504/00 | Fixed roof | FLUSHING OIL | Prioritas 2 | Operation | Surat DIMET No. 519/7819/BK-CRB (BEBAS TERA) | 2045-11-28 | Valid | 2025-12-16 | 4180-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2029-05-31 | Valid | 1485/PKTN.4.8/KHP/DL/05/2019 | Good | All functional |  |  | Good | Standard | Penggantian baru unit transmitter DM4N-2-1 tgl 10//08/2022 |  | Good | Standard | Penggantian baru unit transmitter DM4N-2-1 tgl 10//08/2022 |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-UTL | RU06-UTL -TEN -POWER | 51-T-101/00 | Fixed roof | Diesel Oil | Prioritas 2 | Operation |  |  | Valid | 2025-12-16 | 4182-02-ENI/180/E03-L11/PI/2021 | Expired | Valid |  |  | Valid |  | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-UTL | RU06-UTL -DIST -INTAKE | 53-T-301A/00 | Fixed roof | Fuel Oil Tank | Prioritas 2 | Operation | Local Indicator | 2045-11-28 | Valid | 2025-12-16 | 4183-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2029-02-28 | Valid | 717/PKTN.4.8/KHP/DL/03/2019 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-UTL | RU06-UTL -DIST -INTAKE | 53-T-301B/00 | Fixed roof | Fuel Oil Tank | Prioritas 2 | Operation | Local Indicator | 2045-11-28 | Valid | 2025-12-16 | 4184-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2029-02-28 | Valid | 716/PKTN.4.8/KHP/DL/03/2019 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-UTL | RU06-UTL -TEN -FUEL | 62-T-201A/00 | Fixed roof | Fuel Oil Tank | Prioritas 2 | Operation | Mentoring at DCS System | 2045-11-28 | Valid | 2025-12-16 | 4185-02-ENI/180/E03-L11/P1/2021 | Expired | Valid |  | 2027-07-19 | Valid | TU.6730/PKTN.4.5/DL/08/2025 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-UTL | RU06-UTL -TEN -FUEL | 62-T-201B/00 | Fixed roof | Fuel Oil Tank | Prioritas 2 | Operation | Mentoring at DCS System | 2045-11-28 | Valid | 2025-12-16 | 4186-02-ENI/180/E03-L11/PI/2021 | Expired | Valid |  | 2027-07-19 | Valid | TU.6729/PKTN.4.5/DL/08/2025 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA | I/P jobplan (LPS Tahap 3) |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VI Balongan | RU06-ITP | RU06-ITP -LEY | 63-T-110/00 | Fixed roof | RECOVERED OIL | Prioritas 2 | Operation | Local Indicator | 2045-11-28 | Valid | 2030-04-15 | P013.NH.EW.028.26 | Valid | Valid |  | 2029-09-30 | Valid | 3395/PKTN.4.8/KHP/DL/10/2019 | NA | NA |  |  | Good | Standard |  |  | Good | Standard |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | NA | NA |  |  | Good | Functional |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA | belum dilakukan pemasangan | akan dilakukan pemasangan pada tahap selanjutnya | NA | NA |  |  | Good | Within the range of -0.85 to -1.5 V |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Functional |  |  | Good | Good |  |  | Good | Lifetimhhhhte ≥ 3 years, no damage |  |  | Good | Lifetime ≥ 3 years, no damage |  |  | Good | Functional |  |  | Good | <25% from standard, no significant settlement |  |  | Good | Properly aligned and in good condition |  |  | Good | Operational |  |  | Good | Functional |  |  | NA | NA |  |  | NA | NA |  |  | NA | NA |  |  | Good | Good, no significant corrosion |  |  | Good | Functional |  |  | 2026-07-31
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-01/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Overhaul/Cleaning | TU.3971_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2026-08-11 | 11766-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 2032-11-01 | Valid | TU.3957/PKTN.4.5/KHP/DL/12/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-02/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | TU.3973_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2026-08-11 | 11767-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 2032-11-02 | Valid | TU.3956/PKTN.4.5/KHP/DL/12/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  | General corrosion, berlubang (not- leaking) | Perbaikan wrapping | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-03/00 | Spherical Tank | LIGHT NAPHTHA | Prioritas 3 | Operation | NA | NA | Valid | 2026-08-11 | 11776-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 31 Desember 1999 | Valid | 0148/25/EX/03/2022 | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  | Telah dilakukan Re-Coating keseluruhan tangki |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  | Telah dilakukan perbaiikan |  | Good |  |  |  | Good |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-04/00 | Spherical Tank | LIGHT NAPHTHA | Prioritas 3 | Operation | NA | NA | Valid | 2026-08-11 | 11777-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 31 Desember 1999 | Valid | 0149/25/EX/03/2022 | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  | Telah dilakukan Re-Coating keseluruhan tangki |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  | Telah dilakukan perbaiikan |  | Good |  |  |  | Good |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-05/00 | Floating roof | HEAVY NAPHTHA | Prioritas 3 | Operation | T.103/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2028-11-19 | 0236/SQ/ST/XII/2024 | Valid | Valid |  | 01 Januari 2033 | Valid | 510.3/UPTD-MIL/I/2023 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-06/00 | Floating roof | SWEET NAPHTHA | Prioritas 3 | Operation | T.100/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2028-11-19 | 0237/SQ/ST/XII/2024 | Valid | Overdue < 3 tahun |  | 01 Februari 2032 | Valid | TU. 686/PKTN.4.8/KHP/DL/03/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-07/00 | Floating roof | REFORMATE | Prioritas 3 | Operation | T.102/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2026-08-11 | 11768-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 01 Juni 2032 | Valid | T.430/PKTN.4.8/KHP/DL/06/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-08/00 | Floating roof | REFORMATE | Prioritas 3 | Operation | T.99/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2026-08-11 | 11769-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 01 Februari 2032 | Valid | TU. 677/PKTN.4.8/KHP/DL/03/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-10/00 | Floating roof | GASOLINE | Prioritas 1 | Operation | TU.3976_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2028-11-19 | 0238/SQ/ST/XII/2024 | Valid | Valid |  | 01 Februari 2032 | Valid | TU. 687/PKTN.4.8/KHP/DL/03/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-11/00 | Floating roof | GASOLINE | Prioritas 1 | Operation | TU.3974_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2026-08-03 | 9908-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 2032-11-01 | Valid | TU.3958/PKTN.4.5/KHP/DL/12/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-12/00 | Floating roof | GASOLINE | Prioritas 1 | Operation | TU.3969_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2026-08-03 | 9909-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 2032-11-02 | Valid | TU.3959/PKTN.4.5/KHP/DL/12/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good With Note | terjadi kebocoran shell 3 titik & tebal thickness shell < min thickness.req (sudah dilakukan perbaikan menggunakan metode wrapping) |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good With Note |  | Coating terkelupas & korosi >40% | Re-Coating | Good |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-13/00 | Fixed roof | KEROSENE | Prioritas 2 | Operation | T.101/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2028-11-19 | 0239/SQ/ST/XII/2024 | Valid | Valid |  | 2030-11-01 | Valid | 924 /PKTN.4.8/KHP/DL/12/2020 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-14/00 | Fixed roof | KEROSENE | Prioritas 2 | Operation | T.104/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2028-11-19 | 0240/SQ/ST/XII/2024 | Valid | Valid |  | 01 Februari 2032 | Valid | TU. 688/PKTN.4.8/DL/02/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-15/00 | Fixed roof | KEROSENE | Prioritas 2 | Operation | T.108/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2028-11-19 | 0241/SQ/ST/XII/2024 | Valid | Valid |  | 01 Februari 2032 | Valid | TU. 689/PKTN.4.8/DL/03/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-16/00 | Fixed roof | DIESEL FUEL | Prioritas 2 | Operation | TU.3978_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2028-11-19 | 0241/SQ/ST/XII/2024 | Valid | Valid |  | 01 Februari 2030 | Valid | 122 /PKTN.4.8/KHP/DL/02/2020 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-17/00 | Fixed roof | DIESEL FUEL | Prioritas 2 | Operation | TU.3970_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2028-11-19 | 0243/SQ/ST/XII/2024 | Valid | Valid |  | 2034-09-02 | Valid | T.197/PKTN.4.5.KHP/DL/09/2024 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-18/00 | Fixed roof | DIESEL FUEL | Prioritas 2 | Overhaul/Cleaning | TU.3979_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2028-11-19 | 0244/SQ/ST/XII/2024 | Valid | Valid |  | 01 Februari 2032 | Valid | TU. 691/PKTN.4.8/DL/03/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-20/00 | Fixed roof | RESIDUE | Prioritas 1 | Overhaul/Cleaning | TU.3972_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2026-08-11 | 11770-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 01 Mei 2027 | Valid | TU. 697/PKTN.4.8/KHP/DL/03/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | NA |  |  |  | 2026-07-31
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-21/00 | Fixed roof | RESIDUE | Prioritas 1 | Operation | TU.3977_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2026-08-11 | 11771-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 2031-11-30 | Valid | TU.15188/PKTN.4.5/DL/12/2025 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  | Overhaul | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  | NO ISSUE |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-22/00 | Fixed roof | RESIDUE | Prioritas 1 | Operation | TU.3975_PKTN.4.5_DL_09_2024 | 2026-09-13 | Valid | 2026-08-11 | 11772-02-ENI/138/E08-L11/P1/2022 | Valid | Overdue < 3 tahun |  | 01 Mei 2027 | Valid | TU. 695/PKTN.4.8/KHP/DL/03/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good With Note |  | Roof plate berlubang | Perbaikan wrapping, menunggu eksekusi OH, Sudah dilakukan perbaikan temporary | Good |  |  |  | Good |  |  |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-23/00 | Fixed roof | SLOP OIL | Prioritas 3 | Operation | T.107/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2026-08-11 | 11773-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 2030-11-01 | Valid | 3776 /PKTN.4.8/KHP/DL/12/2020 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-24/00 | Fixed roof | SLOP OIL | Prioritas 3 | Overhaul/Cleaning | T.106/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2026-08-11 | 11774-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 01 Februari 2032 | Valid | TU. 692/PKTN.4.8/KHP/DL/03/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  | Telah dilakukan perbaikan roof wrapping | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-25/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | T.109/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2026-08-11 | 11775-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 01 Februari 2032 | Valid | TU. 693/PKTN.4.8/DL/03/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  | OH | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  |  |  | 2026-07-22
RU VII Kasim | RU07-OFF | RU07-OFF -STAT | 5-T-26/00 | Fixed roof | CRUDE OIL | Prioritas 1 | Operation | T.105/PKTN.4.5/SKHP/DL/08/2023 | 2027-04-17 | Valid | 2026-08-03 | 9910-02-ENI/138/E08-L11/P1/2022 | Valid | Valid |  | 01 Februari 2032 | Valid | TU. 694/PKTN.4.8/KHP/DL/03/2022 | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | NA |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | Good |  |  |  | NA |  | NO ISSUE |  | Good |  |  |  | Good |  |  |  | NA |  |  |  | 2026-07-22